## 2 - Instructions
ASSET MANAGEMENT MASTER ASSET DATA CAPTURE SPREADSHEET - V04.04_20190919
1. Overview
1.1 This spreadsheet nominates the master asset data required to be captured for all projects, asset validation, condition assessments and equipment status updates.
1.2 For projects, all asset data is to be collected via this spreadsheet.
1.3 For other asset management audits all asset data is to be collected via this spreadsheet or through the use of Archibus mobile applications.
1.4 Mandatory and non-mandatory data fields within each tab are highlighted by the colour of the cell headings on each spreadsheet. Colour coding is as listed below.
1.5 This master asset data capture spreadsheet includes multiple tabs which assist in the collection and verficiation of the asset data. Further details on the use of each tab can be found below.
2. Instructions Tab
2.1 Provides high level instructions on overall use of the spreadsheet
3. Master Equipment Standards Tab
3.1 Provides the detailed hard services equipment standards and descriptions for all assets
3.2 Lists the applicable category that each equipment standard is assigned to.
3.3 Identifies if the equipment standard requires statutory maintenance, non-statutory maintenance or has no routine maintenance (NRM)
3.3 Identifies the type of equipment code identifiaction (ie, virtual, item, count, unique bar code), required for each asset based on the assigned equipment standard.
3.4 For assets requiring unique bar codes, identifies the location of where the unique barcode label shall be affixed for each asset.
3.5 Identifies mandatory information to be captured in the comments column for each asset.
3.6 Where equipment types are required to be included that are not currently provided with an Equipment Standard , identify the issue and request a new equipment standard to be issued. If in doubt ask.
4. Modifications Tab | Mandatory Field | Non-Mandatory Field | Highlight modified data fields |  | Drop-Down Field | Auto-Generated Field
4.1 Used to capture all changes to asset data currently available for each asset included in the Tab 9 - Existing Asset Register
4.2 For each asset identified as requiring data changes, copy the full row from the Tab 9 - Existing Asset Register, and make the required data modifications, ensuring that all fields and data modified is highlighted.
4.3 Note that this tab contains an additional column to the other data capture spreadsheet tabs. The additional column is to identify any changes from the original equipment code to a new equipment code. This needs to be tracked carefully to ensure asset history remains with any incorrectly coded assets or assets requiring new unique bar codes.
4.4 This tab shall be used to capture all changes to data against existing assets, including adding additional manadatory data where none currently exists. All mandatory fields shall be populated as part of the asset validation process.
4.5 Where an existing asset has a unique barcode assigned to it, a new barcode shall not be assigned without seeking approval from the University. This is to prevent individual assets having multiple barcodes assigned to them.
4.6 This tab shall NOT be used for new assets (use Tab 5 - Additions).
4.7 This tab shall NOT be used for assets that could not be found during the asset validation or those that remain on site but have been decommissioned or are not in service (use Tab 6 - Deactivations)
5. Additions Tab | Mandatory Field | Non-Mandatory Field | Drop-Down Field | Auto-Generated Field
5.1 Used to capture new assets installed during project work or asset found during asset audits that are not listed in the Tab 9 - Existing Asset Register
5.2 All mandatory fields listed in the spreadsheet shall be populated.
5.3 In cases where new assets are installed to replace existing assets, the existing asset must be captured under the deactivation tab, with explanatory notes provided in Column A of both spreadsheets
6. Deactivations Tab | Mandatory Field | Non-Mandatory Field | Drop-Down Field | Auto-Generated Field
6.1 Used to capture assets that could not be found during the asset validation and those assets that remain on site but have been decommissioned or are no longer active.
6.2 Also used to deactivate assets at the commencement of a project to take assets out of service for the construction period while they are not operational and do not require maintenance. Provide proposed period of deactivation in Column A.
6.3 For each asset identified as deactivated, copy the full row from Tab 9 - Existing Asset Register and make the required change to the Equipment Status field as per Tab 8 - Equipment Status Table.
6.4 Explanatory notes must be provided in column A of the deactivations tab as to the reasoning for listing the asset as deactivated, together with any supporting documentation, ie photos, etc.
7. Assessment Tables
7.1 These tables provide definitions for the numerical values required to be provided in the appropriate fields on the Modifications, Additions and Deactivations tab spreadsheets.
7.2 The fields these tables represent is mandatory data for all assets.
7.3 Please ensure all staff performing asset validations and condition assessments are fully aware of the definitions of these fields and the importance of providing a consistent assessemnts for these fields across all assets. If in doubt ask.
8. Status Table
8.1 This table provides definitions for the status of assets, required in the appropriate fields on the Modifications, Additions and Deactivations tab spreadsheets,
8.2 The status field is mandatory data for all assets.
9. Asset Register
9.1 The current asset register for the space and equipment category requested.
9.2 This sheet is locked from being edited but may be copied for reference in the other tabs.
9.3 This sheet will change for each project or asset validation being performed.

## 3 - Master Equipment Standards
TAB 3 - MASTER EQUIPMENT STANDARDS
Equipment Category | Equipment Standard Description | Equipment Standard Code |  | Maintenance Type, ie, Statutory, Non-Statutory, No Routine Maintenance (NRM) | Unique Equipment Code Type, ie, Unique Bar Code, Virtual or Item Count | Unique bar code label location | Unique bar code number range | Mandatory information to be captured in comments field
EQSTD.CATEGORY | EQSTD.DESCRIPTION | EQSTD.EQ_STD |  | EQSTD.SECURITY_GROUP | EQSTD.OPTION1 | EQSTD.OPTION2 | EQSTD.OPTION3 | EQ.COMMENTS
CATEGORY | EQUIPMENT STANDARD DESCRIPTION | EQUIPMENT STANDARD | SUBCOMPONENT OF | SECURITY_GROUP | OPTION1 | OPTION2 | OPTION3 | COMMENTS | Categories | Number Range | Categories | ListName | ACCESS EQUIPMENT | AUTO DOORS & SHUTTERS | BMS | CRANES & HOISTS | EEL | ELECTRICAL | EXTERIORS | FAÇADE | FFE | FFE LAB | FFE SAFETY | FFE SPECIALIST | FIRE | FUME CUPBOARD | GROUNDS | ICT AV | INTERIORS | LIFT | LOCKSMITH | MECHANICAL | MEDICAL AND LAB GASSES | PLUMBING | RELAMPING & LIGHTING | ROOF & GUTTER | ROOF SAFETY | SECURITY ELECTRONIC | STRUCTURE | SUBSTRUCTURE | TRAFFIC | WASTE | WATER TREATMENT
ACCESS EQUIPMENT | Cherry Picker | 27700 |  | Statutory | Unique Bar Code | On Control Panel | 7 Million | Load capacity and driver type | ACCESS EQUIPMENT | 7 Million | ACCESS EQUIPMENT | Access | Cherry Picker | Auto Speed Stiles | BMS Control Panel | Building Maintenance Unit (BMU) | Emergency Light- Test Switch | Auto Transfer Switch | External Balustrades | Aluminium Composite Panels | 2 Seater Lounge | -30c Freezer | Bio-Hazard Safety Cabinet | Band Saw | A/C Fire Trip-Automatic Shutdown | Fume Cupboard Fan | Boardwalks | Audio Amplifier | Automated Operable Shading Louvre | Dumb Waiter | Bilock Campus | Air and Dirt Separator | Bulk Gas - Argon | Access Chamber | Downlight Compact Fluorescent CFL/PLC Single Lamp | Access Hatch | Access Platform | Access Door | Awning | Concrete Structure | Carparking Payment Machine | Bin Internal | Boiler Softener
ACCESS EQUIPMENT | Elevated Work Platform | 30103 |  | Statutory | Unique Bar Code | On Control Panel | 7 Million | Load capacity and driver type | AUTO DOORS & SHUTTERS | 8 Million | AUTO DOORS & SHUTTERS | Autodoors | Elevated Work Platform | Battery Backup Emergency Exit System |  | Crane Electric Gantry | Emergency Light-Central Battery Luminaires | Body Protected Electrical Area Test Switch | External Handrails | External Glazed Pivot Doors | 2.5 Seater Lounge | -80c Freezer | Dangerous Goods Cabinet | CNC Router | Annual Condition Report | Fume Cupboard Hydrofluoric Acid | Bollards | Document Camera | Bathroom Partitions | Escalators | Bilock General | Air Conditioning Unit - Air Cooled Packaged Ducted | Bulk Gas - Carbon Dioxide | Accessible Shower | Downlight Compact Fluorescent CFL/PLC Twin Lamps | Box Gutter | Anchor Point | Aperio Door | Shade Structures | Footings | Carparking Space | External Large Mobile Bin | Chemical Dosing Pot Condenser loop
ACCESS EQUIPMENT | Walkie Stacker | 30104 |  | Statutory | Unique Bar Code | On Control Panel | 7 Million | Load capacity and driver type | BMS | 6 Million | BMS | BMS | Hydraulic Jack Trolley | Door Auto Slide Operation |  | Crane Jib | Emergency Lighting-Central Battery System | Busbar Power Rail | External Painting | External Glazing | 3 Seater Lounge | Balance | Flammable Goods Cabinet | Electric Bed | Annual Fire Safety Statement | Fume Cupboard Perchloric Acid | Decks | Hearing Loop | Blinds - Manual | Lift motor | Safe | Air Conditioning Unit - Air Cooled Split Condenser | Bulk Gas - High Purity Nitrogen | Air Admittance Valve | Downlight LED Lamp | Concrete Roof | Davit Arm | CCTV Camera - External | Skylight | Piled Wall |  | Garbage Bin - 15 litre | Chemical Dosing Pot Heating loop
ACCESS EQUIPMENT | Hydraulic Jack Trolley | 30105 |  | Statutory | Unique Bar Code | On Handle | 7 Million |  | CRANES & HOISTS | 7 Million | CRANES & HOISTS | Cranes | Robot Forklift | Door Auto Swing Inward Operation |  | Crane Manual Gantry | Emergency Lighting-Computer Monitored System | Cardiac Protected Electrical Area Test Switch | Powder Coated Finishes | Louvres - Operable | Accessible Study Desk | Biomedical Freezer | Laminar Flow Cabinet | Exercise Stairs | Damper - Fire | Fume Cupboard Recirculated Type | Driveways | ICT Projector | Blinds - Motorised | Passenger Lift Hydraulic |  | Air Conditioning Unit - Air Cooled Split FCU Ducted | Bulk Gas - Nitrogen | Backflow Prevention Device | Downlight MR16, Dichroic Halogen Lamp | Copper Roof | Fall Arrest Barriers | CCTV Camera - Internal | Structural Steel | Retaining Wall |  | Garbage Bin - 25 litre | Chemical Dosing Station (Automatic Dosing)
ACCESS EQUIPMENT | Robot Forklift | 30106 |  | Statutory | Unique Bar Code | On Control Panel | 7 Million |  | EEL | 3 Million | EEL | EEL | Walkie Stacker | Door Auto Swing Outward Operation |  | Derrick | Emergency Light-Luminaires No Test Switch | Ceiling Fan |  | Metal Cladding | Accessible Underbench Oven | Biomedical Fridge |  | Gym Equipment | Damper - Smoke | Fume Cupboard Scrubber | External Bike Rack | ICT Projector Screen | Compactus | Passenger Lift Motor Room Less (MRL) |  | Air Conditioning Unit - Air Cooled Split indoor | Gas Sensor - Crabon Dioxide | Bath | Downlight Parabolic Aluminised Reflector PAR Halogen Lamp | External Waterproof Membrane | Fixed Ladder | Duress Button |  | Termite Protection |  | Garbage Bin - 50 litre | Cooling Tower - Closed Loop
AUTO DOORS & SHUTTERS | Door Roller Manual Operation | 15236 |  | Non-Statutory | Unique Bar Code | Adjacent Operating Device | 8 Million | Size and operating mechanism | ELECTRICAL | 3 Million | ELECTRICAL | Electrical |  | Door Roller Manual Operation |  | Hoist Electric | Emergency Light-Luminaires with Test Switch | Ceiling Fan\Light |  | Pre-cast Concrete Panels | AMX Control Panel | Blotting Machine |  | Laser Cutter | Detector - CO | Fume Cupboard Standard | External Bins | Interactive LCD | Curtains | Passenger Lift Traction |  | Air Conditioning Unit - Portable | Gas Sensor - LEL | Boiling & Chilled Water Unit | Exterior Halogen Box Floodlights | Gutter/Downpipe | Ladder Bracket | DVR |  |  |  | Public Space External Fixed Bin | Cooling Tower - Open
AUTO DOORS & SHUTTERS | Security Grille/Shutter | 15237 |  | Non-Statutory | Unique Bar Code | On Shutter | 8 Million | Size and operating mechanism | EXTERIORS | 1 Million | EXTERIORS | Exteriors |  | Door Roller Motorised Operation |  | Hoist Manual | Exit Light-Central Battery Luminaires | Clock |  | Shading Elements | AV Speakers & Surround Sound System | Bunsen Burner |  | Milling Machine | Detector - Flame | Fume Cupboard VSD | External Furniture | IR Hearing Augmentation System | Entrance Mat | Signage-Warning Signage for Passenger Lifts |  | Air Conditioning Unit - Room Window or Wall-mounted | Gas Sensor - Oxygen Depletion | Boiling Water Unit | Exterior LED Floodlight | Metal Roof | Static Lines | Electronic Security Controller |  |  |  | Waste Bin - 135 litre | Pump Chemical Dosing
AUTO DOORS & SHUTTERS | Auto Speed Stiles | 15238 |  | Non-Statutory | Unique Bar Code | On Stile | 8 Million | Size and operating mechanism | FAÇADE | 1 Million | FAÇADE | Facade |  | Gate Motorised Operation |  | Lift Table Hydraulic | Exit Light-Luminaires No Test Switch | Control Panel - Windows, Roller Shutter, etc. |  | Stone Panels | Bar Fridge | Cardiac Monitor |  | Mobile Lift | Detector - Heat - Linear |  | External Paving | Lecturn | Flooring Carpet | Wheelchair Lift Car |  | Air Conditioning Unit - Water Cooled Ducted Package Unit | Liquid Nitrogen Dewar | Boundary Trap | Exterior Metal Halide Floodlight | Rain Water Head | Walkway | Emergency Help Point |  |  |  | Wheelie Bin - 60 litre | Water Treatment Sand Filter
AUTO DOORS & SHUTTERS | Door Auto Slide Operation | 15239 |  | Non-Statutory | Unique Bar Code | On Controller | 8 Million | Size and operating mechanism | FFE | 1 Million | FFE | FFE |  | Security Grille/Shutter |  | Lifting Gear General | Exit Light-Luminaires with Test Switch | Distribution Switchboard |  | Timber Cladding | Bar Stool | Cell Analyser |  | Pedestal Drill | Detector - Heat - Linear Concealed |  | Fixed Barbeque (BBQ) | Microphone | Flooring Carpet Tiles | Wheelchair Lift Platform |  | Air Conditioning Unit - Water Cooled Floor Console Unit | Liquid Nitrogen Tank | Boundary Valve | Heritage Feature Light | Roof - Mixed Fabric |  | Glass Break Detector
AUTO DOORS & SHUTTERS | Gate Motorised Operation | 15240 |  | Non-Statutory | Unique Bar Code | On Controller | 8 Million | Size and operating mechanism | FFE LAB | 9 Million | FFE LAB | FFELab |  |  |  | Monorail |  | Electrical General (Sub Board) |  |  | Bathroom Light\Fan\Heater | Cell Counter |  | Recumbent Bike | Detector - Heat - Point |  | Footpaths | Recording Camera and Mount | Flooring Concrete |  |  | Air Conditioning Unit - Water Cooled Split Condenser | Medical Air | Boundary Valve With PRV | High/Low Bay Fluorescent Light | Slate Roof |  | Glass Furnace Alarm
AUTO DOORS & SHUTTERS | Door Roller Motorised Operation | 15243 |  | Non-Statutory | Unique Bar Code | On Controller | 8 Million | Size and operating mechanism | FFE SAFETY | 9 Million | FFE SAFETY | FFESafety |  |  |  | Trolley Electric |  | Electrical Meter |  |  | Bean Bag | Cell Dissociator |  | Rowing Ergometer | Detector - Heat - Point Concealed |  | Garden Beds | USB Camera | Flooring Flake Polyurethane |  |  | Air Conditioning Unit - Water Cooled Split FCU Duc | Medical and Lab Gas Monitor/Panel | Cleaners Tap | High/Low Bay induction Lamp | Tile Roof |  | Passive Infrared Sensor
AUTO DOORS & SHUTTERS | Door Auto Swing Inward Operation | 15244 |  | Non-Statutory | Unique Bar Code | On Controller | 8 Million | Size and operating mechanism | FFE SPECIALIST | 9 Million | FFE SPECIALIST | FFESpecialist |  |  |  | Trolley Manual |  | Essential Services Switchboard |  |  | Bedside Table | Cell Printer |  | Treadmill | Detector - Smk - Aspirating |  | Irrigation Controller | Wall Mounted Display Panel | Flooring Malthoid |  |  | Air Conditioning Unit - Water Cooled Split indoor | Medical and Laboratory Gas Valve Set | Cold Water Pump | High/Low Bay LED Light | Valley/Ridge |  | PSU
AUTO DOORS & SHUTTERS | Door Auto Swing Outward Operation | 15245 |  | Non-Statutory | Unique Bar Code | On Controller | 8 Million | Size and operating mechanism | FIRE | 4 Million | FIRE | Fire |  |  |  | Winch Electric |  | Generator |  |  | Billiard Table | Centrifuge |  |  | Detector - Smk - Linear |  | Lawns |  | Flooring Marble |  |  | Air Cooled Reciprocating Chiller | Medical Nitous Oxde | Control Valve Gas | High/Low Bay Mecury Vapour Light |  |  | Reciever
AUTO DOORS & SHUTTERS | Battery Backup Emergency Exit System | 15246 |  | Statutory | Unique Bar Code | Adjacent Battery | 8 Million | Number, type and date of batteries | FUME CUPBOARD | 2 Million | FUME CUPBOARD | Fume |  |  |  | Winch Manual |  | Generator Inlet |  |  | Blue-Ray Player | Clinical Chemistry Auto Analyser |  |  | Detector - Smk - Linear Concealed |  | Pavements |  | Flooring Moasonite |  |  | Air Cooled Screw Chiller | Medical Oxygen | Control Valve Water | High/Low Bay Metal Halide Light |  |  | Reed Switch
BMS | BMS Control Panel | 11438 |  | Non-Statutory | Unique Bar Code | On Front Of Panel | 6 Million | Site labelling name | GROUNDS | 5 Million | GROUNDS | Grounds | [5 empty] | Generator Outlet |  |  | Booth Lounge | Combustible Liquids Cabinet |  |  | Detector - Smk - Point Concealed |  | Planter Boxes |  | Flooring Painted Concrete |  |  | Air Cooled Scroll Chiller | Speciality Gas Cabinet | Decorative Fountain | Incandescent Globe Light |  |  | Remote Release
CRANES & HOISTS | Crane Jib | 14406 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity | ICT AV | 1 Million | ICT AV | ICT | [5 empty] | Generator Outlet Twin |  |  | Café Side Table | Corrosive Cabinet |  |  | Detector - Smk - Projected beam |  | Roads |  | Flooring Paving |  |  | Air Curtain |  | Decorative Fountain Pump | Isle Light |  |  | Secured Lifts
CRANES & HOISTS | Hoist Manual | 14429 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity, number of floors | INTERIORS | 1 Million | INTERIORS | Interiors | [5 empty] | Generator Switchboard |  |  | Chesterfield Sofa | Cryotome |  |  | Detector Smk - Point |  | Signs |  | Flooring Pebble |  |  | Air Filter - Absolute |  | Dry Basket Arrestor | Linear Led Tube/Strip Single |  |  | Security BMS Alarm
CRANES & HOISTS | Lift Table Hydraulic | 14431 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity, height | LIFT | 7 Million | LIFT | Lift | [5 empty] | Lift Switchboard |  |  | Clothes Dryer | CT Scanning Unit |  |  | Domestic Heat Alarm |  | Sporting Fields |  | Flooring Polished Concrete |  |  | Air Filter - Activated Carbon |  | Emergency Eye Wash Facility | Linear Led Tube/Strip Twin |  |  | Security Fire Trip Alarm
CRANES & HOISTS | Monorail | 14432 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity, height | LOCKSMITH | 8 Million | LOCKSMITH | Locksmith | [5 empty] | Lighting Control (CBUS Control) |  |  | Clothes Washing Machine | Cytospin |  |  | Domestic Smoke Alarm |  | Trees |  | Flooring Rubber |  |  | Air Filter - Auto Roll |  | Emergency Safety Shower | Modern Feature Light |  |  | Security Gas Alarm
CRANES & HOISTS | Crane Electric Gantry | 14433 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity, height | MECHANICAL | 2 Million | MECHANICAL | Mechanical | [5 empty] | Lighting Control (Dynalite Control) |  |  | Coffee Table | Dangerous Drugs Safe |  |  | Duct probe smoke detector |  |  |  | Flooring Sand |  |  | Air Filter - Bag Throw Away |  | Envirocycle Sewerage System | Occupancy Sensor Hybrid Type |  |  | Security Temperature Alarm
CRANES & HOISTS | Hoist Electric | 14434 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity, height | MEDICAL AND LAB GASSES | 9 Million | MEDICAL AND LAB GASSES | Medical | [5 empty] | Lightning Protection System |  |  | Computer Tables with Central Divider & Cable Tray. | DNA Sequencing |  |  | Egress-Evacuation Plans |  |  |  | Flooring Soil |  |  | Air Filter - Deep Bed |  | Expansion Tank | Occupancy Sensor Microwave Type
CRANES & HOISTS | Winch Manual | 14435 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity, height | PLUMBING | 5 Million | PLUMBING | Plumbing | [5 empty] | Load Centre |  |  | Dart Board | Electroporator |  |  | Egress-Exit/Egress Doors |  |  |  | Flooring Tarket |  |  | Air Filter - Electrostatic |  | External Fountain Drinking | Occupancy Sensor PIR Type
CRANES & HOISTS | Winch Electric | 14436 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity, height | RELAMPING & LIGHTING | 3 Million | RELAMPING & LIGHTING | Relamping | [5 empty] | Load Management System |  |  | Desk Lamp | Evaporator-Concentrator |  |  | Egress-Paths of Travel to Exits & Exit Stairs |  |  |  | Flooring Terrazzo |  |  | Air Filter - Grease |  | Flusherette Tank | Occupancy Sensor Ultrasonic Type
CRANES & HOISTS | Trolley Manual | 14437 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity | ROOF & GUTTER | 7 Million | ROOF & GUTTER | Roof | [5 empty] | Main Switchboard |  |  | Dining Chair | Flammable Liquids Cabinet |  |  | Egress-Power Operated Exit Doors |  |  |  | Flooring Tiles |  |  | Air Filter - HEPA |  | Fountain | Road/Path Fluorescent LED Street Light
CRANES & HOISTS | Trolley Electric | 14438 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity | ROOF SAFETY | 7 Million | ROOF SAFETY | RoofSafety | [5 empty] | Manual Transfer Switch |  |  | Dining Chair with Arms | Fragment Bioanalyser |  |  | Egress-Security Door Interface |  |  |  | Flooring Timber |  |  | Air Filter - Metal Frame Pleated |  | Gas Meter | Road/Path Fluorescent Vapour Street Light
CRANES & HOISTS | Lifting Gear General | 14439 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity | SECURITY ELECTRONIC | 8 Million | SECURITY ELECTRONIC | Security | [5 empty] | Non Ducted Exhaust Fan |  |  | Dining Table | Freeze Dryer |  |  | EWIS / OWS Speakers |  |  |  | Flooring Vinyl |  |  | Air Filter - Metal Frame Washable |  | Grease Trap | Road/Path lighting Kim Archetype External Light Metal Halide Lamp
CRANES & HOISTS | Derrick | 14440 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity | STRUCTURE | 1 Million | STRUCTURE | Structure | [5 empty] | Power Factor Correction |  |  | Dishwasher | Gel Imaging System |  |  | EWIS Panel |  |  |  | Internal Balustrades |  |  | Air Filter - Panel Throw Away |  | Greywater Treatment System | Road/Path lighting Kim Bounce Pole Light >4M LED Luminaire
CRANES & HOISTS | Building Maintenance Unit (BMU) | 14441 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity | SUBSTRUCTURE | 1 Million | SUBSTRUCTURE | Substructure | [5 empty] | Power Start / Stop Station |  |  | Domestic Freezer | Growth Cabinet |  |  | Extinguisher-Aerosol |  |  |  | Internal Glazed Doors |  |  | Air Filter - Panel washable |  | Gross Pollutant Trap | Road/Path lighting Kim Bounce Pole Light >4M Metal Halide Lamp
CRANES & HOISTS | Crane Manual Gantry | 14442 |  | Statutory | Unique Bar Code | TBD | 7 Million | Load capacity | TRAFFIC | 8 Million | TRAFFIC | Traffic | [5 empty] | Regional Switchboard |  |  | Domestic Range Hood | Homogeniser |  |  | Extinguisher-CO2 |  |  |  | Internal Glazing |  |  | Air Handling Unit |  | Hand Basin - Accessible | Road/Path lighting Kim Bounce Pole Light <4M LED Luminaire
EEL | Emergency Light-Central Battery Luminaires | 13301 |  | Statutory | Unique Bar Code | On Fitting | 3 Million | Lamp type | WASTE | 1 Million | WASTE | Waste | [5 empty] | Residual Current Device 10mA (Medical and lab RCD`s) |  |  | Domestic Refrigerator | HPLC System |  |  | Extinguisher-Foam |  |  |  | Internal Handrails |  |  | Air Receiver |  | Hand Basin - General | Road/Path lighting Kim Bounce Pole Light <4M Metal Halide Lamp
EEL | Exit Light-Central Battery Luminaires | 13302 |  | Statutory | Unique Bar Code | On Fitting | 3 Million | Lamp type | WATER TREATMENT | 2 Million | WATER TREATMENT | Water | [5 empty] | Residual Current Device 30mA |  |  | Drum Seating | Imager |  |  | Extinguisher-Non Recharge |  |  |  | Internal Painting |  |  | Air Scrubber (non fume cabinet) |  | Hand Basin - Lab | Road/Path lighting Louis Polsen Pole Light <4m Metal Halide Lamp
EEL | Emergency Lighting-Central Battery System | 13303 |  | Statutory | Unique Bar Code | On Charger | 3 Million | Number and type of batteries | [9 empty] | Residual Current Device Other |  |  | Electric Cooktop | Incubator |  |  | Extinguisher-Powder |  |  |  | Internal Waterproof Membrane |  |  | Airflow Valve |  | Hose Cock | Road/Path lighting Louis Polsen Pole Light >4m Metal Halide Lamp
EEL | Emergency Light-Luminaires with Test Switch | 13304 |  | Statutory | Unique Bar Code | On Fitting | 3 Million | Battery type and date, lamp type, addressable device number | [9 empty] | Room Heater - Electric Convection |  |  | Electric Oven | Lab Freezer |  |  | Extinguisher-Vapourizing Liq |  |  |  | Joinery |  |  | Autoclave - Electric (Fixed units only) |  | Hose Tap | Road/Path Mercury Vapour Street Light
EEL | Exit Light-Luminaires with Test Switch | 13305 |  | Statutory | Unique Bar Code | On Fitting | 3 Million | Battery type and date, lamp type, addressable device number | [9 empty] | Room Heater - Electric Radiant |  |  | Electronic Signage | Lab Fridge |  |  | Extinguisher-Water |  |  |  | Manual Operable Shading Louvre |  |  | Autoclave - Gas (Fixed units only) |  | Hot Water - Heat Exchanger | Road/Path Sodium Vapour Street Light
EEL | Emergency Light-Luminaires No Test Switch | 13306 |  | Statutory | Unique Bar Code | On Fitting | 3 Million | Battery type and date, lamp type, addressable device number | [9 empty] | Soft Wired Workstation |  |  | Fixed Clothes Line | Lab Mixer |  |  | Extinguisher-Wet Chem |  |  |  | Operable Walls |  |  | Autoclave - Steam (Fixed units only) |  | Hot Water Pump (Recirculating) | Seat Light
EEL | Exit Light-Luminaires No Test Switch | 13307 |  | Statutory | Unique Bar Code | On Fitting | 3 Million | Battery type and date, lamp type, addressable device number | [9 empty] | Solar Panels PV |  |  | Fixed TV | Light Source |  |  | Extinguisher-Wheeled |  |  |  | Stair Nosings |  |  | Blow Down Tank - Steam |  | Hot Water Storage Tank | Sports Field Flood Lighting
EEL | Emergency Lighting-Computer Monitored System | 13308 |  | Statutory | Unique Bar Code | On PC and Monitor | 3 Million | Number fittings monitored | [9 empty] | Solar PV Inverter |  |  | Floor Lamp | Microscope |  |  | FIP - Addressable |  |  |  | Suspended Ceilings |  |  | Boiler Hot Water Heating - Electric |  | HWU Electric | Step Light
EEL | Emergency Light- Test Switch | 13309 |  | Statutory | Unique Bar Code | Adjacent Switch | 3 Million | Switchboard number | [9 empty] | Substation |  |  | Floor Mounted Bike Rack | MRI Machine |  |  | FIP - Conventional |  |  |  | Tactile Indicators |  |  | Boiler Hot Water Heating - Gas |  | HWU Gas | T12 Single
ELECTRICAL | Room Heater - Electric Convection | 11301 |  | Non-Statutory | Unique Bar Code | Adjacent Switch | 3 Million | Site labelling name | [9 empty] | Surge Protected Fault Test Switch |  |  | Fryer | Muliplex Bead Assay Reader |  |  | FIP - Gas System |  |  |  | Timber Doors |  |  | Boiler Steam - Electric |  | Laundry Sink | T12 Triple
ELECTRICAL | Room Heater - Electric Radiant | 11302 |  | Non-Statutory | Unique Bar Code | Adjacent Switch | 3 Million | Site labelling name | [9 empty] | UPS |  |  | Game Console | PCR Instrument |  |  | FIP - Local Alarm Indicator | [6 empty] | Boiler Steam - Gas |  | Natural Gas Double Outlet | T12 Twin
ELECTRICAL | Lighting Control (CBUS Control) | 14305 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | Addressable device number | [9 empty] | UPS outlet |  |  | Gas Cooktop | pH Meter |  |  | FIP - Mimic | [6 empty] | Calorifier |  | Natural Gas Flue | T5 Single
ELECTRICAL | Lighting Control (Dynalite Control) | 14306 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | Addressable device number | [9 empty] | UPS Outlet Double |  |  | Gas Oven | Pipette Aid |  |  | FIP - Repeater | [6 empty] | Car Park C0 Sensor |  | Natural Gas Regulator | T5 Triple
ELECTRICAL | Control Panel - Windows, Roller Shutter, etc. | 14313 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | Details of asset being controlled | [12 empty] | Hand Dryer - Dyson Air Blade | Plate Reader |  |  | Fire / Smoke Damper | [6 empty] | Chilled Beam - Active |  | Natural Gas Shut Off Valve | T5 Twin
ELECTRICAL | Auto Transfer Switch | 14314 |  | Non-Statutory | Unique Bar Code | Adjacent Switch | 3 Million | Switchboard number | [12 empty] | Hand Wash Dispenser | Plate Washer |  |  | Fire Alarm Sounder | [6 empty] | Chilled Beam - Passive |  | Natural Gas Single Outlet | T8 Single
ELECTRICAL | Generator | 14337 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 3 Million | Engine capacity and output | [12 empty] | Hexagonal Tables | Robotic Workstation |  |  | Fire Blanket | [6 empty] | Chilled water Storage Tank |  | Non Potable Lab Water Storage Tank | T8 Triple
ELECTRICAL | Generator Inlet | 14338 |  | Non-Statutory | Virtual Bar Code | [15 empty] | High Bench Stool | Scintillation Counter |  |  | Fire fan and damper controls | [6 empty] | Chiller - Air Cooled Centrifugal |  | On Site Detention Tank | T8 Twin
ELECTRICAL | Generator Outlet | 14339 |  | NRM | Virtual Bar Code | [15 empty] | High Stool | Shaker |  |  | Fire Hose Reel-30 metre | [6 empty] | Chiller - Water Cooled Centrifugal |  | Potable Water Storage Tank
ELECTRICAL | Generator Outlet Twin | 14340 |  | NRM | Virtual Bar Code | [15 empty] | Ice Machine | Sonicator |  |  | Fire Hose Reel-36 metre | [6 empty] | Compressed Air Air Dryer |  | Rain Water Storage Tank
ELECTRICAL | UPS | 14341 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 3 Million | Output capacity, number, type and date of batteries | [12 empty] | Indoor Ottoman | Spectrophotometer |  |  | Fire Hose Reel-50 metre | [6 empty] | Compressor - Air |  | Rain Water Treatment Plant
ELECTRICAL | UPS outlet | 14342 |  | NRM | Virtual Bar Code | [15 empty] | Indoor\Outdoor Ottoman | Toxic Liquids Cabinet |  |  | Fire Hydrant General System | [6 empty] | Compressor - Refrigeration (For remote compressors only) |  | Rainwater Filter - First Flush
ELECTRICAL | UPS Outlet Double | 14343 |  | NRM | Virtual Bar Code | [15 empty] | King Single Bed | Vacuum Pumps |  |  | Fire Hydrant Tank | [6 empty] | Compressor - Vacuum |  | Reflux Valve
ELECTRICAL | Power Start / Stop Station | 14346 |  | Non-Statutory | Unique Bar Code | Adjacent Switch | 3 Million | Details of asset being controlled | [12 empty] | King Single Bunk bed | Water Purifier |  |  | Fire Monitoring (ASE) | [6 empty] | Computer Room Air Conditioning Unit - Air Cooled |  | Reverse Osmosis Unit
ELECTRICAL | Busbar Power Rail | 14347 |  | NRM | Virtual Bar Code | [15 empty] | Large Rectangular Rug | Waterbath |  |  | Fire Monitoring System Computer & Display | [6 empty] | Computer Room Air Conditioning Unit - Water Cooled |  | Sensor Taps
ELECTRICAL | Soft Wired Workstation | 14350 |  | NRM | Virtual Bar Code | [15 empty] | Large Round Rug | X-Ray Machine |  |  | Fire Sprinkler Tank | [6 empty] | Condensate Pump |  | Sewer Pit
ELECTRICAL | Surge Protected Fault Test Switch | 14353 |  | Non-Statutory | Unique Bar Code | Adjacent Switch | 3 Million | Size | [12 empty] | Laundry Table | X-Ray Viewer |  |  | Fire Sprinkler/Hydrant Tank | [6 empty] | Condenser Pump - Primary or Secondary |  | Sewer Pump
ELECTRICAL | Load Management System | 14354 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 3 Million | Software details | [12 empty] | Liquid Kitchen Washing Dispenser |  |  |  | Fume cupboard thermal duct probe | [6 empty] | Condensing Unit Cool Room - Water-Cooled |  | Sewerage Treatment Plant
ELECTRICAL | Manual Transfer Switch | 14355 |  | Non-Statutory | Unique Bar Code | Adjacent Switch | 3 Million | Switchboard number | [12 empty] | Lockers |  |  |  | Gas Fire Ext Sys-Argonite | [6 empty] | Condensing Unit Coolroom Room - Air Cooled |  | Shower General
ELECTRICAL | Substation | 14370 |  | NRM | Unique Bar Code | Adjacent Substation Number | 3 Million | Substation capacity, site labelling name | [12 empty] | Lounge Arm Chair |  |  |  | Gas Fire Ext Sys-CO2 | [6 empty] | Condensing Unit Environmental Control Room - Air C |  | Silt Arrestor
ELECTRICAL | Regional Switchboard | 14371 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | Site labelling name, number of poles | [12 empty] | Lounge Chair |  |  |  | Gas Fire Ext Sys-FE 13 | [6 empty] | Condensing Unit Environmental Control Room - Water |  | Sink Cleaner
ELECTRICAL | Main Switchboard | 14372 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | Site labelling name, number of poles | [12 empty] | Meeting Room Table |  |  |  | Gas Fire Ext Sys-FM200 | [6 empty] | Condensing Unit Freezer Room - Air Cooled |  | Sink Kitchen
ELECTRICAL | Lift Switchboard | 14374 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | Site labelling name, number of poles | [12 empty] | Microwave |  |  |  | Gas Fire Ext Sys-Inert Gas | [6 empty] | Condensing Unit Freezer Room - Water-Cooled |  | Sink Lab
ELECTRICAL | Generator Switchboard | 14375 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | Site labelling name, number of poles | [12 empty] | Mobile Pedestal |  |  |  | Gas Fire Ext Sys-NAFSIII | [6 empty] | Control - Pneumatic System |  | Solar Panels Hot water
ELECTRICAL | Essential Services Switchboard | 14376 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | Site labelling name, number of poles | [12 empty] | Organic Bench Seating |  |  |  | Gas Fire Ext Sys-Pyrogen | [6 empty] | Control Sensor - Gas |  | Solar Panels Storage Tank
ELECTRICAL | Distribution Switchboard | 14377 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | Site labelling name, number of poles | [12 empty] | Organic Table |  |  |  | Gas Fire Ext Sys-Water Mist | [6 empty] | Control Sensor - Humidity |  | Storm Water Grated Drain
ELECTRICAL | Load Centre | 14378 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | Size and capacity | [12 empty] | Ottoman |  |  |  | Gas Fire Ext Sys-Wet Chemical | [6 empty] | Control Sensor - PIR |  | Storm Water Pit
ELECTRICAL | Electrical General (Sub Board) | 14379 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | Site labelling name, number of poles | [12 empty] | Outdoor Kitchen |  |  |  | Hyd-Booster Connection | [6 empty] | Control Sensor - Pressure |  | Storm Water Pump
ELECTRICAL | Residual Current Device 30mA | 14380 |  | Statutory | Unique Bar Code | Adjacent Switch | 3 Million | Switchboard and circuit breaker number | [12 empty] | Paper Towel Dispenser |  |  |  | Hyd-Landing Valves-Single | [6 empty] | Control Sensor - Temperature |  | Submersible Pump
ELECTRICAL | Residual Current Device 10mA (Medical and lab RCD`s) | 14381 |  | Statutory | Unique Bar Code | Adjacent Switch | 3 Million | Switchboard and circuit breaker number | [12 empty] | Pinball Machine |  |  |  | Hyd-Landing Valves-Twin | [6 empty] | Control Sensor - Velocity |  | Subsoil Filter - Bag
ELECTRICAL | Residual Current Device Other | 14382 |  | Statutory | Unique Bar Code | Adjacent Switch | 3 Million | Switchboard and circuit breaker number | [12 empty] | Projector |  |  |  | Hyd-Monitored Valve | [6 empty] | Cooling Tower - Closed Loop |  | Taps General
ELECTRICAL | Body Protected Electrical Area Test Switch | 14383 |  | Statutory | Unique Bar Code | Adjacent Switch | 3 Million | Switchboard and circuit breaker number | [12 empty] | Projector Screen |  |  |  | Hyd-Spk – Combined System Booster Connection | [6 empty] | Cooling Tower - Open |  | Taps Lab
ELECTRICAL | Cardiac Protected Electrical Area Test Switch | 14384 |  | Statutory | Unique Bar Code | Adjacent Switch | 3 Million | Switchboard and circuit breaker number | [12 empty] | Queen Bed |  |  |  | Lay Flat Fire Hose | [6 empty] | Cooling tower - Sand Filter |  | Tempering Valve
ELECTRICAL | Non Ducted Exhaust Fan | 14400 |  | NRM | Unique Bar Code | On Cover | 3 Million | [13 empty] | Queen Bunk bed |  |  |  | Magnetic Door Holder | [6 empty] | Coolroom |  | Thermostatic Mixing Valve
ELECTRICAL | Ceiling Fan | 14401 |  | NRM | Unique Bar Code | On Cover | 3 Million | [13 empty] | Rectangular High Counter Bench |  |  |  | Manual Call Point (Red) | [6 empty] | Damper - Balancing |  | Trade Waste Cooling Pit
ELECTRICAL | Clock | 14402 |  | NRM | Unique Bar Code | On Cover | 3 Million | Analog or digital | [12 empty] | Rectangular Ottoman |  |  |  | Manual Call Point (White) | [6 empty] | Damper - General |  | Trade Waste Dilution Pit
ELECTRICAL | Power Factor Correction | 14405 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | Site labelling name | [12 empty] | Single Seater Lounge |  |  |  | Mass Notification System Computer & Display | [6 empty] | Damper - Motorised |  | Trade Waste General Purpose Trap Pit
ELECTRICAL | Lightning Protection System | 14407 |  | Non-Statutory | Virtual Bar Code |  |  | System type | [12 empty] | Sit and Stand Desk - Manual |  |  |  | Occupant Warning System | [6 empty] | Damper - Relief Air |  | Urinal
ELECTRICAL | Solar Panels PV | 14554 |  | Non-Statutory | Unique Bar Code | On Frame Near Cable Entry | 3 Million | Size and output | [12 empty] | Sit and Stand Desk - Powered |  |  |  | Passive - Double Fire Door | [6 empty] | Damper - Spilled Air |  | Urinal Flush Sensor
ELECTRICAL | Solar PV Inverter | 14555 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | Number of panels connected | [12 empty] | Steel Coffee Table |  |  |  | Passive - Double Smoke Door | [6 empty] | Dehumidifier - DX |  | Urinal Trough Type
ELECTRICAL | Electrical Meter | 14556 |  | Non-Statutory | Unique Bar Code | On Cover | 3 Million | AUMS device number, ownership | [12 empty] | Study Chair |  |  |  | Passive - Fire Curtain | [6 empty] | Dehumidifier - Elec |  | Urinal Waterless
ELECTRICAL | Ceiling Fan\Light | 33230 |  | NRM | Count/Room |  |  | Lamp type and size | [12 empty] | Study Desk Lamp |  |  |  | Passive - Smoke Curtain | [6 empty] | Dehumidifier - Gas |  | Waste Oil Tank
EXTERIORS | External Balustrades | 43001 |  | Non-Statutory | Count/Building |  |  | Area (m2) | [12 empty] | Study Table |  |  |  | Passive Fire-Fire Shutter | [6 empty] | Duct Heater - Electric |  | Waste Water Treatment Plant
EXTERIORS | External Handrails | 43002 |  | Non-Statutory | Count/Building |  |  | Lineal metres | [12 empty] | Table Tennis table |  |  |  | Passive-Access Panels | [6 empty] | Ducted Gas Heater or Furnace for HVAC System |  | Water Filter - Automatic Backwash
EXTERIORS | External Painting | 43003 |  | Non-Statutory | Count/Building |  |  | Area (m2) | [12 empty] | Task Chair |  |  |  | Passive-Barrier-Bulkhead | [6 empty] | Dust Extraction Unit |  | Water Filter - Cartridge Type
EXTERIORS | Powder Coated Finishes | 43004 |  | Non-Statutory | Count/Building |  |  | Area (m2) | [12 empty] | Task Chair with Arms - Accessible |  |  |  | Passive-Barrier-Ceiling | [6 empty] | Electric Humidifier |  | Water Filter - UV
FAÇADE | Pre-cast Concrete Panels | 41001 |  | Non-Statutory | Count/Building |  |  | Area (m2) | [12 empty] | Toilet Roll Holder - Common Bathrooms |  |  |  | Passive-Barrier-Floor | [6 empty] | Environmental Control Room |  | Water Filter Bag Type
FAÇADE | Stone Panels | 41002 |  | Non-Statutory | Count/Building |  |  | Area (m2) | [12 empty] | Toilet Roll Holder - Accessible and Ambulant Toilets |  |  |  | Passive-Barrier-Wall | [6 empty] | Evaporative Cooler |  | Water Meter
FAÇADE | Aluminium Composite Panels | 41003 |  | Non-Statutory | Count/Building |  |  | Area (m2) | [12 empty] | Wall Mounted Bike Rack |  |  |  | Passive-Beam/Column/Truss | [6 empty] | Evaporator - Coolroom |  | Water Purification Unit
FAÇADE | Metal Cladding | 41004 |  | Non-Statutory | Count/Building |  |  | Area (m2) | [12 empty] | Wall Mounted Fan (Domestic Style) |  |  |  | Passive-Ceiling Hatches | [6 empty] | Evaporator - Environmental Control Room |  | WC Pan - Accessible
FAÇADE | Timber Cladding | 41005 |  | Non-Statutory | Count/Building |  |  | Area (m2) | [12 empty] | White Board |  |  |  | Passive-Ducts | [6 empty] | Evaporator - Freezer Room |  | WC Pan - Ambulatory
FAÇADE | Louvres - Operable | 41006 |  | Non-Statutory | Count/Floor |  |  | Area (m2) | [12 empty] | Wire Basket |  |  |  | Passive-Fire Door-Hinged | [6 empty] | Expansion Tank Chilled Water - Gravity |  | WC Pan - General
FAÇADE | Shading Elements | 41007 |  | Non-Statutory | Count/Floor |  |  | Area (m2) | [12 empty] | Workstation |  |  |  | Passive-Fire Door-Sliding | [6 empty] | Expansion Tank Chilled Water - Pressurised
FAÇADE | External Glazing | 41008 |  | Non-Statutory | Count/Building |  |  | Area (m2) | [16 empty] | Passive-Glazing | [6 empty] | Expansion Tank Hot Water - Gravity
FAÇADE | External Glazed Pivot Doors | 41009 |  | Non-Statutory | Unique Bar Code | Door Jamb | 1 Million | Size, hardware | [16 empty] | Passive-Smoke Door-Hinged | [6 empty] | Expansion Tank Hot Water - Pressurised
FFE | Fryer | 33110 |  | NRM | Unique Bar Code | On Control Panel | 1 Million | Electric or gas | [16 empty] | Passive-Solid Core Doors | [6 empty] | Extraction Arm
FFE | Microwave | 33118 |  | NRM | Unique Bar Code | On Control Panel | 1 Million | [17 empty] | Passive-Stopping-Cntrl Joints | [6 empty] | Fan Coil Unit - Ducted. Chilled, Hot Water or Electric Heating
FFE | Fixed TV | 33134 |  | NRM | Unique Bar Code | On Control Panel | 1 Million | [17 empty] | Passive-Stopping-Damper Seal | [6 empty] | Fan Coil Unit - Gas Heating
FFE | Domestic Refrigerator | 33138 |  | NRM | Unique Bar Code | Adjacent Nameplate | 1 Million | Volume | [16 empty] | Passive-Stopping-Penetration | [6 empty] | Fan Coil Unit - Non Ducted. Chilled, Hot Water or Electric Heating
FFE | Domestic Freezer | 33139 |  | NRM | Unique Bar Code | Adjacent Nameplate | 1 Million | Volume | [16 empty] | Pumpset-Hose Reel | [6 empty] | Fan Exhaust Air
FFE | Gas Oven | 33141 |  | NRM | Unique Bar Code | On Control Panel | 1 Million | [17 empty] | Pumpset-Hydrant-Combined Diesel/Electric | [6 empty] | Fan Filter Unit
FFE | Ice Machine | 33142 |  | NRM | Unique Bar Code | On Control Panel | 1 Million | [17 empty] | Pumpset-Hydrant-Diesel | [6 empty] | Fan Pressurisation
FFE | Gas Cooktop | 33145 |  | NRM | Unique Bar Code | On Control Panel | 1 Million | Number burners | [16 empty] | Pumpset-Hydrant-Electric | [6 empty] | Fan Relief Air
FFE | Electric Cooktop | 33146 |  | NRM | Unique Bar Code | On Control Panel | 1 Million | Number burners | [16 empty] | Pumpset-Jacking Pump | [6 empty] | Fan Return Air
FFE | Electric Oven | 33147 |  | NRM | Unique Bar Code | On Control Panel | 1 Million | [17 empty] | Pumpset-Residential-Diesel | [6 empty] | Fan Roof-Mounted - Exhaust
FFE | Electronic Signage | 33158 |  | NRM | Virtual Bar Code | [19 empty] | Pumpset-Residential-Electric | [6 empty] | Fan Roof-Mounted - Supply
FFE | Clothes Washing Machine | 33159 |  | NRM | Unique Bar Code | On Control Panel | 1 Million | Volume | [16 empty] | Pumpset-Sprinkler/Hydrant-Diesel | [6 empty] | Fan Smoke Spill
FFE | Toilet Roll Holder - Common Bathrooms | 33169 |  | NRM | Count/Room | [19 empty] | Pumpset-Sprinkler/Hydrant-Electric | [6 empty] | Fan Spilled Air
FFE | Paper Towel Dispenser | 33170 |  | NRM | Count/Room | [19 empty] | Pumpset-Sprinkler-Combined Diesel/Electric | [6 empty] | Fan Supply Air
FFE | Hand Wash Dispenser | 33171 |  | NRM | Count/Room | [19 empty] | Pumpset-Sprinkler-Diesel | [6 empty] | Fan Window or Wall-Mounted - Supply or Exhaust Air
FFE | Liquid Kitchen Washing Dispenser | 33172 |  | NRM | Count/Room | [19 empty] | Pumpset-Sprinkler-Electric | [6 empty] | Freezer Room
FFE | Hand Dryer - Dyson Air Blade | 33178 |  | NRM | Unique Bar Code | Adjacent Nameplate | 1 Million | Cold or warm air | [16 empty] | Signage-Fire Safety Notice | [6 empty] | Gas Humidifier
FFE | Domestic Range Hood | 33180 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 1 Million | Size and capacity | [16 empty] | Signage-Fire, Smoke & Egress Door Signage | [6 empty] | Heat Exchanger - Air To Air
FFE | Dining Table | 33181 |  | NRM | Count/Room | [19 empty] | Specalist fire trip | [6 empty] | Heat Exchanger - Plate
FFE | Laundry Table | 33182 |  | NRM | Count/Room | [19 empty] | Sprinkler Sys - Deluge Valve | [6 empty] | Heat Exchanger - Shell & Tube
FFE | Coffee Table | 33183 |  | NRM | Count/Room | [19 empty] | Sprinkler Sys - Dry Pipe Valve | [6 empty] | Heater - Gas Convection
FFE | Meeting Room Table | 33184 |  | NRM | Count/Room | [19 empty] | Sprinkler Sys - Pre-Action Valve | [6 empty] | Heater - Gas Radiant
FFE | Study Table | 33185 |  | NRM | Count/Room | [19 empty] | Sprinkler Sys-Alarm Valve | [6 empty] | HVAC UV light fixtures
FFE | Bedside Table | 33186 |  | NRM | Count/Room | [19 empty] | Sprinkler Sys-Booster Connection | [6 empty] | Incinerator
FFE | Workstation | 33187 |  | NRM | Count/Room | [19 empty] | Sprinkler Sys-Flow Switches | [6 empty] | Inertia Tank - Chilled Water
FFE | High Bench Stool | 33188 |  | NRM | Count/Room | [19 empty] | Sprinkler Sys-Monitored Valve | [6 empty] | Inertia Tank - Hot Water
FFE | Dining Chair | 33189 |  | NRM | Count/Room | [19 empty] | Sprinkler Sys-PreAct-Air Compressor | [6 empty] | Kitchen Exhaust Hood
FFE | Task Chair | 33190 |  | NRM | Count/Room | [19 empty] | Sprinkler Sys-Wall Wetting | [6 empty] | Kitchen Exhuast Fan
FFE | Lounge Chair | 33191 |  | NRM | Count/Room | [19 empty] | Sprinkler-Deluge Sys | [6 empty] | Mechanical Services Control Panel
FFE | 3 Seater Lounge | 33192 |  | NRM | Count/Room | [19 empty] | Sprinkler-Domestic Sys | [6 empty] | Mechanical Services Switchboard
FFE | 2 Seater Lounge | 33193 |  | NRM | Count/Room | [19 empty] | Sprinkler-Dry Pipe Sys | [6 empty] | Pump Chilled Water - Primary or Secondary
FFE | Lounge Arm Chair | 33194 |  | NRM | Count/Room | [19 empty] | Sprinkler-General Sys | [6 empty] | Pump Heating Water - Primary or Secondary
FFE | Task Chair with Arms - Accessible | 33196 |  | NRM | Count/Room | [19 empty] | Sprinkler-Pre-Action Sys | [6 empty] | Refrigerant Detection Unit
FFE | Drum Seating | 33197 |  | NRM | Count/Room | [19 empty] | Sprinkler-Residential Sys | [6 empty] | Sensible Cooling Coil
FFE | 2.5 Seater Lounge | 33198 |  | NRM | Count/Room | [19 empty] | Sprinkler-Water Spray Sys | [6 empty] | Smoke & Heat Vents
FFE | Organic Bench Seating | 33199 |  | NRM | Count/Room | [19 empty] | Vesda | [6 empty] | Smoke Control-Zone Pressurisation System
FFE | Study Chair | 33200 |  | NRM | Count/Room | [19 empty] | Visual Warning Device (Strobe) | [6 empty] | Special Exhaust Hood
FFE | Indoor\Outdoor Ottoman | 33201 |  | NRM | Count/Room | [19 empty] | Warden Intercom Phone | [6 empty] | Stair Pressurisation Fan
FFE | Ottoman | 33202 |  | NRM | Count/Room | [26 empty] | Steam Trap
FFE | Indoor Ottoman | 33203 |  | NRM | Count/Room | [26 empty] | Supply / Exhuast Air Valve
FFE | Chesterfield Sofa | 33204 |  | NRM | Count/Room | [26 empty] | Thermal Ceiling Diffuser
FFE | Bar Stool | 33205 |  | NRM | Count/Room | [26 empty] | VAV Box
FFE | Booth Lounge | 33206 |  | NRM | Count/Room | [26 empty] | Ventilated Cabinet/Workbench
FFE | Rectangular Ottoman | 33207 |  | NRM | Count/Room | [26 empty] | VRV Air Cooled Condenser
FFE | Bean Bag | 33208 |  | NRM | Count/Room | [26 empty] | VRV Air Cooled Gas Driven Condenser
FFE | King Single Bed | 33213 |  | NRM | Count/Room | [26 empty] | VRV Branch Control Unit
FFE | Queen Bed | 33214 |  | NRM | Count/Room | [26 empty] | VRV Control Panel
FFE | King Single Bunk bed | 33215 |  | NRM | Count/Room | [26 empty] | VRV Split FCU Ducted
FFE | Queen Bunk bed | 33216 |  | NRM | Count/Room | [26 empty] | VRV Split indoor single FCU
FFE | Floor Lamp | 33217 |  | NRM | Count/Room |  |  | Lamp type and size | [23 empty] | VRV Water Cooled Condenser
FFE | Desk Lamp | 33218 |  | NRM | Count/Room |  |  | Lamp type and size | [23 empty] | VRV Water Cooled Gas Driven Condenser
FFE | Large Rectangular Rug | 33219 |  | NRM | Count/Room | [26 empty] | VSD
FFE | Large Round Rug | 33220 |  | NRM | Count/Room | [26 empty] | Water Cooled Gas Driven Screw Chiller
FFE | Projector | 33221 |  | Non-Statutory | Unique Bar Code | On Control Panel | 1 Million | [24 empty] | Water cooled Reciprocating Chiller
FFE | Projector Screen | 33222 |  | Non-Statutory | Count/Room |  |  | Size | [23 empty] | Water Cooled Screw Chiller
FFE | Fixed Clothes Line | 33224 |  | NRM | Count/Room | [26 empty] | Water cooled Scroll Chiller
FFE | Lockers | 33225 |  | NRM | Count/Room | [26 empty] | Wind Powered Roof Ventilator
FFE | Billiard Table | 33226 |  | NRM | Count/Room
FFE | Table Tennis table | 33227 |  | NRM | Count/Room
FFE | AV Speakers & Surround Sound System | 33231 |  | NRM | Count/Room
FFE | Blue-Ray Player | 33232 |  | NRM | Unique Bar Code | On Control Panel | 1 Million
FFE | AMX Control Panel | 33233 |  | NRM | Unique Bar Code | On Control Panel | 1 Million
FFE | Game Console | 33234 |  | NRM | Unique Bar Code | On Control Panel | 1 Million
FFE | Pinball Machine | 33235 |  | NRM | Unique Bar Code | On Control Panel | 1 Million
FFE | Dart Board | 33236 |  | NRM | Count/Room
FFE | Wall Mounted Fan (Domestic Style) | 33237 |  | NRM | Virtual Bar Code
FFE | White Board | 33238 |  | NRM | Count/Room |  |  | Size
FFE | Wire Basket | 33245 |  | NRM | Count/Room
FFE | Mobile Pedestal | 33246 |  | NRM | Count/Room
FFE | Bar Fridge | 33247 |  | NRM | Unique Bar Code | Adjacent Nameplate | 1 Million | Volume
FFE | Accessible Underbench Oven | 33251 |  | NRM | Unique Bar Code | On Control Panel | 1 Million
FFE | Dishwasher | 33252 |  | NRM | Unique Bar Code | Adjacent Nameplate | 1 Million | Volume
FFE | Café Side Table | 33253 |  | NRM | Count/Room
FFE | Rectangular High Counter Bench | 33254 |  | NRM | Count/Room
FFE | Computer Tables with Central Divider & Cable Tray. | 33255 |  | NRM | Count/Room
FFE | Hexagonal Tables | 33256 |  | NRM | Count/Room
FFE | Steel Coffee Table | 33257 |  | NRM | Count/Room
FFE | Organic Table | 33258 |  | NRM | Count/Room
FFE | Accessible Study Desk | 33260 |  | NRM | Count/Room
FFE | Single Seater Lounge | 33261 |  | NRM | Count/Room
FFE | Dining Chair with Arms | 33262 |  | NRM | Count/Room
FFE | High Stool | 33263 |  | NRM | Count/Room
FFE | Wall Mounted Bike Rack | 33274 |  | NRM | Count/Room
FFE | Floor Mounted Bike Rack | 33275 |  | NRM | Count/Room
FFE | Study Desk Lamp | 33279 |  | NRM | Count/Room |  |  | Lamp type and size
FFE | Outdoor Kitchen | 33284 |  | NRM | Count/Room
FFE | Toilet Roll Holder - Accessible and Ambulant Toilets | 33291 |  | NRM | Count/Room
FFE | Bathroom Light\Fan\Heater | 33298 |  | NRM | Count/Room |  |  | Lamp type and size
FFE | Sit and Stand Desk - Powered | 33301 |  | NRM | Unique Bar Code | On Frame Near Control Panel | 1 Million
FFE | Sit and Stand Desk - Manual | 33302 |  | NRM | Unique Bar Code | On Frame | 1 Million
FFE | Clothes Dryer | 33303 |  | NRM | Unique Bar Code | On Control Panel | 1 Million
FFE LAB | Growth Cabinet | 33150 |  | Non-Statutory | Unique Bar Code | On Control Panel | 9 Million | Class type
FFE LAB | -80c Freezer | 33151 |  | Non-Statutory | Unique Bar Code | On Control Panel | 9 Million | Alarm details
FFE LAB | Incubator | 33152 |  | Non-Statutory | Unique Bar Code | On Control Panel | 9 Million | Type (Drosophola, Live Rodents, Bacterial, Mammalian)
FFE LAB | Flammable Liquids Cabinet | 48001 |  | Statutory | Unique Bar Code | On Front Door Near Handle | 9 Million | Size and capacity
FFE LAB | Corrosive Cabinet | 48002 |  | Statutory | Unique Bar Code | On Front Door Near Handle | 9 Million | Size and capacity
FFE LAB | Combustible Liquids Cabinet | 48003 |  | Statutory | Unique Bar Code | On Front Door Near Handle | 9 Million | Size and capacity
FFE LAB | Toxic Liquids Cabinet | 48004 |  | Statutory | Unique Bar Code | On Front Door Near Handle | 9 Million | Size and capacity
FFE LAB | Vacuum Pumps | 48051 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Biomedical Freezer | 48101 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Volume
FFE LAB | Biomedical Fridge | 48101 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Volume
FFE LAB | Lab Freezer | 48103 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Volume
FFE LAB | Lab Fridge | 48104 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Volume
FFE LAB | -30c Freezer | 48105 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Balance | 48201 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Type (analytical, computer, standard)
FFE LAB | Blotting Machine | 48202 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Cell Analyser | 48203 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Type
FFE LAB | Centrifuge | 48204 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Type (bench, tissue culture), Size and Speed
FFE LAB | Clinical Chemistry Auto Analyser | 48205 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Cryotome | 48206 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Type (LN Dispenser, LN Vapour Phase)
FFE LAB | Cytospin | 48207 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Electroporator | 48208 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Evaporator-Concentrator | 48209 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Fragment Bioanalyser | 48210 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Freeze Dryer | 48211 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Gel Imaging System | 48212 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Homogeniser | 48213 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | HPLC System | 48214 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Imager | 48215 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Light Source | 48218 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | pH Meter | 48219 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Microscope | 48220 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Type
FFE LAB | Lab Mixer | 48221 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Type
FFE LAB | Muliplex Bead Assay Reader | 48222 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | PCR Instrument | 48223 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Pipette Aid | 48224 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Plate Reader | 48225 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Specification
FFE LAB | Plate Washer | 48226 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Robotic Workstation | 48227 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Scintillation Counter | 48228 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Type (Harvester, Microplate, Vial)
FFE LAB | Sonicator | 48229 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Type
FFE LAB | Spectrophotometer | 48230 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Water Purifier | 48231 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Waterbath | 48232 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Type and Size
FFE LAB | Cell Printer | 48233 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Shaker | 48234 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Type
FFE LAB | Bunsen Burner | 48235 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Cell Counter | 48236 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Cell Dissociator | 48237 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | DNA Sequencing | 48238 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | Dangerous Drugs Safe | 48239 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Size
FFE LAB | Cardiac Monitor | 48301 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | X-Ray Viewer | 48302 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | CT Scanning Unit | 48303 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | X-Ray Machine | 48304 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE LAB | MRI Machine | 48305 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE SAFETY | Bio-Hazard Safety Cabinet | 33148 |  | Statutory | Unique Bar Code | On Control Panel | 9 Million | Class type
FFE SAFETY | Laminar Flow Cabinet | 33149 |  | Statutory | Unique Bar Code | On Control Panel | 9 Million | Class type
FFE SAFETY | Flammable Goods Cabinet | 33156 |  | Statutory | Unique Bar Code | On Door | 9 Million | Size and capacity
FFE SAFETY | Dangerous Goods Cabinet | 33157 |  | Statutory | Unique Bar Code | On Door | 9 Million | Size and capacity
FFE SPECIALIST | CNC Router | 49001 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE SPECIALIST | Pedestal Drill | 49002 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE SPECIALIST | Laser Cutter | 49003 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE SPECIALIST | Milling Machine | 49004 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE SPECIALIST | Band Saw | 49005 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE SPECIALIST | Recumbent Bike | 49101 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE SPECIALIST | Rowing Ergometer | 49102 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE SPECIALIST | Gym Equipment | 49103 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Type
FFE SPECIALIST | Treadmill | 49104 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE SPECIALIST | Exercise Stairs | 49105 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million
FFE SPECIALIST | Electric Bed | 49151 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Type
FFE SPECIALIST | Mobile Lift | 49152 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 9 Million | Type, Size, Weight Capacity
FIRE | Damper - Fire | 11231 |  | Statutory | Unique Bar Code | On Access Panel | 4 Million | Site labelling name
FIRE | Damper - Smoke | 11232 |  | Statutory | Unique Bar Code | On Access Panel | 4 Million | Site labelling name
FIRE | Annual Fire Safety Statement | 12000 |  | Statutory | Unique Bar Code | Adjacent Framed AFSS | 4 Million
FIRE | Annual Condition Report | 12001 |  | Statutory | Virtual Bar Code
FIRE | FIP - Conventional | 12100 |  | Statutory | Unique Bar Code | On Control Panel | 4 Million | FMS device number, battery number, size and date
FIRE | FIP - Addressable | 12101 |  | Statutory | Unique Bar Code | On Control Panel | 4 Million | FMS device number, battery number, size and date
FIRE | FIP - Mimic | 12102 |  | Statutory | Unique Bar Code | On Control Panel | 4 Million | FMS device number, battery number, size and date
FIRE | FIP - Repeater | 12103 |  | Statutory | Unique Bar Code | On Control Panel | 4 Million | FMS device number, battery number, size and date
FIRE | FIP - Local Alarm Indicator | 12104 |  | Statutory | Unique Bar Code | On Control Panel | 4 Million | FMS device number, battery number, size and date
FIRE | FIP - Gas System | 12105 |  | Statutory | Unique Bar Code | On Control Panel | 4 Million | FMS device number, battery number, size and date
FIRE | Vesda | 12106 |  | Statutory | Unique Bar Code | On Control Panel | 4 Million | FMS device number, battery number, size and date
FIRE | Manual Call Point (Red) | 12107 |  | Statutory | Unique Bar Code | On Housing | 4 Million | Addressable device number
FIRE | EWIS Panel | 12108 |  | Statutory | Unique Bar Code | On Control Panel | 4 Million | MNS device number, battery number, size and date
FIRE | Fire Monitoring (ASE) | 12109 |  | Statutory | Unique Bar Code | On Housing | 4 Million | ASE & AFA numbers
FIRE | Detector - Heat - Point | 12110 |  | Statutory | Unique Bar Code | On Base | 4 Million | Addressable device number
FIRE | Detector - Heat - Linear | 12111 |  | Statutory | Unique Bar Code | On Base | 4 Million | Addressable device number
FIRE | Detector Smk - Point | 12112 |  | Statutory | Unique Bar Code | On Base | 4 Million | Addressable device number
FIRE | Detector - Smk - Linear | 12113 |  | Statutory | Unique Bar Code | On Base | 4 Million | Addressable device number
FIRE | Detector - Smk - Aspirating | 12114 |  | Statutory | Unique Bar Code | On Base | 4 Million | Addressable device number
FIRE | Detector - Flame | 12115 |  | Statutory | Unique Bar Code | On Base | 4 Million | Addressable device number
FIRE | Detector - CO | 12116 |  | Statutory | Unique Bar Code | On Base | 4 Million | Addressable device number
FIRE | Domestic Smoke Alarm | 12117 |  | Statutory | Unique Bar Code | On Base | 4 Million
FIRE | Occupant Warning System | 12118 |  | Statutory | Unique Bar Code | On Control Panel | 4 Million | MNS device number
FIRE | EWIS / OWS Speakers | 12119 |  | Statutory | Virtual Bar Code
FIRE | Fire Alarm Sounder | 12120 |  | Statutory | Virtual Bar Code
FIRE | Domestic Heat Alarm | 12121 |  | Statutory | Unique Bar Code | On Base | 4 Million
FIRE | Visual Warning Device (Strobe) | 12122 |  | Statutory | Virtual Bar Code
FIRE | Warden Intercom Phone | 12123 |  | Statutory | Unique Bar Code | On Base | 4 Million | Name on EWIS panel
FIRE | Magnetic Door Holder | 12124 |  | Statutory | Virtual Bar Code
FIRE | Detector - Heat - Point Concealed | 12125 |  | Statutory | Unique Bar Code | On Base | 4 Million | Addressable device number
FIRE | Detector - Heat - Linear Concealed | 12126 |  | Statutory | Unique Bar Code | On Base | 4 Million | Addressable device number
FIRE | Detector - Smk - Point Concealed | 12127 |  | Statutory | Unique Bar Code | On Base | 4 Million | Addressable device number
FIRE | Detector - Smk - Linear Concealed | 12128 |  | Statutory | Unique Bar Code | On Base | 4 Million | Addressable device number
FIRE | Detector - Smk - Projected beam | 12129 |  | Statutory | Unique Bar Code | On Base | 4 Million | Addressable device number
FIRE | Fire Monitoring System Computer & Display | 12130 |  | Non-Statutory | Unique Bar Code | On PC and Monitor | 4 Million | FMS device number and location (ie, gate house)
FIRE | Fire fan and damper controls | 12131 |  | Statutory | Virtual Bar Code |  |  | Number of controls
FIRE | Duct probe smoke detector | 12132 |  | Statutory | Unique Bar Code | On Housing | 4 Million | Addressable device number
FIRE | Fume cupboard thermal duct probe | 12133 |  | Statutory | Unique Bar Code | On Remote Indicator | 4 Million | Addressable device number
FIRE | Specalist fire trip | 12134 |  | Statutory | Virtual Bar Code
FIRE | Mass Notification System Computer & Display | 12135 |  | Non-Statutory | Unique Bar Code | On PC and Monitor | 4 Million | FMS device number and location (ie, gate house)
FIRE | Manual Call Point (White) | 12136 |  | Statutory | Unique Bar Code | On Base | 4 Million | Name on EWIS panel
FIRE | Sprinkler-General Sys | 12200 |  | Statutory | Virtual Bar Code
FIRE | Sprinkler-Pre-Action Sys | 12201 |  | Statutory | Virtual Bar Code
FIRE | Sprinkler-Deluge Sys | 12202 |  | Statutory | Virtual Bar Code
FIRE | Sprinkler-Residential Sys | 12203 |  | Statutory | Virtual Bar Code
FIRE | Sprinkler-Domestic Sys | 12204 |  | Statutory | Virtual Bar Code
FIRE | Sprinkler-Dry Pipe Sys | 12205 |  | Statutory | Virtual Bar Code
FIRE | Sprinkler-Water Spray Sys | 12206 |  | Statutory | Virtual Bar Code
FIRE | Fire Sprinkler Tank | 12207 |  | Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 4 Million | Tank size
FIRE | Sprinkler Sys-PreAct-Air Compressor | 12210 |  | Statutory | Unique Bar Code | On Air Receiver | 4 Million | Pressure capacity
FIRE | Sprinkler Sys-Alarm Valve | 12211 |  | Statutory | Unique Bar Code | Valve Cover | 4 Million | Site labelling name
FIRE | Sprinkler Sys-Flow Switches | 12212 |  | Statutory | Unique Bar Code | Valve Cover | 4 Million | Site labelling name
FIRE | Sprinkler Sys-Booster Connection | 12213 |  | Statutory | Unique Bar Code | Valve Cover | 4 Million | Number of booster inlets and hydrant supply valves
FIRE | Sprinkler Sys-Wall Wetting | 12214 |  | Statutory | Unique Bar Code | Valve Cover | 4 Million | Site labelling name
FIRE | Sprinkler Sys-Monitored Valve | 12215 |  | Statutory | Unique Bar Code | Valve Cover | 4 Million | Addressable device number
FIRE | Sprinkler Sys - Dry Pipe Valve | 12216 |  | Statutory | Unique Bar Code | Valve Cover | 4 Million | Site labelling name
FIRE | Sprinkler Sys - Deluge Valve | 12217 |  | Statutory | Unique Bar Code | Valve Cover | 4 Million | Site labelling name
FIRE | Sprinkler Sys - Pre-Action Valve | 12218 |  | Statutory | Unique Bar Code | Valve Cover | 4 Million | Site labelling name
FIRE | Pumpset-Sprinkler-Electric | 12300 |  | Statutory | Unique Bar Code | On Motor/Engine | 4 Million | Motor capacity, battery number size and date
FIRE | Pumpset-Sprinkler-Diesel | 12301 |  | Statutory | Unique Bar Code | On Motor/Engine | 4 Million | Engine capacity, battery number, size and date
FIRE | Pumpset-Hydrant-Diesel | 12302 |  | Statutory | Unique Bar Code | On Motor/Engine | 4 Million | Engine capacity, battery number, size and date
FIRE | Pumpset-Hydrant-Electric | 12303 |  | Statutory | Unique Bar Code | On Motor/Engine | 4 Million | Motor capacity, battery number size and date
FIRE | Pumpset-Jacking Pump | 12304 |  | Statutory | Unique Bar Code | On Motor/Engine | 4 Million | Motor capacity
FIRE | Pumpset-Residential-Electric | 12305 |  | Statutory | Unique Bar Code | On Motor/Engine | 4 Million | Motor capacity, battery number size and date
FIRE | Pumpset-Residential-Diesel | 12306 |  | Statutory | Unique Bar Code | On Motor/Engine | 4 Million | Engine capacity, battery number, size and date
FIRE | Pumpset-Sprinkler-Combined Diesel/Electric | 12307 |  | Statutory | Unique Bar Code | On Motor/Engine | 4 Million | Engine and motor capacity, battery number size and date
FIRE | Pumpset-Hydrant-Combined Diesel/Electric | 12308 |  | Statutory | Unique Bar Code | On Motor/Engine | 4 Million | Engine and motor capacity, battery number size and date
FIRE | Pumpset-Hose Reel | 12309 |  | Statutory | Unique Bar Code | On Motor/Engine | 4 Million | Motor capacity
FIRE | Pumpset-Sprinkler/Hydrant-Electric | 12310 |  | Statutory | Unique Bar Code | On Motor/Engine | 4 Million | Motor capacity, battery number size and date
FIRE | Pumpset-Sprinkler/Hydrant-Diesel | 12311 |  | Statutory | Unique Bar Code | On Motor/Engine | 4 Million | Engine capacity, battery number, size and date
FIRE | Hyd-Landing Valves-Single | 12400 |  | Statutory | Unique Bar Code | Valve Cover | 4 Million
FIRE | Hyd-Landing Valves-Twin | 12401 |  | Statutory | Unique Bar Code | Valve Cover | 4 Million
FIRE | Hyd-Booster Connection | 12402 |  | Statutory | Unique Bar Code | Valve Cover | 4 Million | Number of booster inlets and hydrant supply valves
FIRE | Fire Hydrant Tank | 12403 |  | Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 4 Million | Tank size
FIRE | Hyd-Monitored Valve | 12404 |  | Statutory | Unique Bar Code | Valve Cover | 4 Million | Addressable device number
FIRE | Fire Hydrant General System | 12405 |  | Statutory | Virtual Bar Code
FIRE | Hyd-Spk – Combined System Booster Connection | 12406 |  | Statutory | Unique Bar Code | Valve Cover | 4 Million | Number of booster inlets and hydrant supply valves
FIRE | Fire Sprinkler/Hydrant Tank | 12407 |  | Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 4 Million | Tank size
FIRE | Fire Hose Reel-30 metre | 12500 |  | Statutory | Unique Bar Code | On Drum | 4 Million
FIRE | Fire Hose Reel-36 metre | 12501 |  | Statutory | Unique Bar Code | On Drum | 4 Million
FIRE | Lay Flat Fire Hose | 12600 |  | Statutory | Unique Bar Code | On Connector | 4 Million
FIRE | Gas Fire Ext Sys-FM200 | 12901 |  | Statutory | Unique Bar Code | On Gas Manifold | 4 Million | Number and size of gas cyliners
FIRE | Gas Fire Ext Sys-Inert Gas | 12902 |  | Statutory | Unique Bar Code | On Gas Manifold | 4 Million | Number and size of gas cyliners
FIRE | Gas Fire Ext Sys-Argonite | 12903 |  | Statutory | Unique Bar Code | On Gas Manifold | 4 Million | Number and size of gas cyliners
FIRE | Gas Fire Ext Sys-CO2 | 12904 |  | Statutory | Unique Bar Code | On Gas Manifold | 4 Million | Number and size of gas cyliners
FIRE | Gas Fire Ext Sys-FE 13 | 12905 |  | Statutory | Unique Bar Code | On Gas Manifold | 4 Million | Number and size of gas cyliners
FIRE | Gas Fire Ext Sys-Wet Chemical | 12906 |  | Statutory | Unique Bar Code | On Gas Manifold | 4 Million | Number and size of gas cyliners
FIRE | Gas Fire Ext Sys-Water Mist | 12907 |  | Statutory | Unique Bar Code | On Gas Manifold | 4 Million | Number and size of gas cyliners
FIRE | Gas Fire Ext Sys-Pyrogen | 12908 |  | Statutory | Unique Bar Code | On Gas Manifold | 4 Million | Number and size of gas cyliners
FIRE | Gas Fire Ext Sys-NAFSIII | 12909 |  | Statutory | Unique Bar Code | On Gas Manifold | 4 Million | Number and size of gas cyliners
FIRE | Fire Hose Reel-50 metre | 12910 |  | Statutory | Unique Bar Code | On Drum | 4 Million
FIRE | Extinguisher-Water | 13101 |  | Statutory | Unique Bar Code | On Type Signage | 4 Million | Size and capacity
FIRE | Extinguisher-Wet Chem | 13102 |  | Statutory | Unique Bar Code | On Type Signage | 4 Million | Size and capacity
FIRE | Extinguisher-Foam | 13103 |  | Statutory | Unique Bar Code | On Type Signage | 4 Million | Size and capacity
FIRE | Extinguisher-Powder | 13104 |  | Statutory | Unique Bar Code | On Type Signage | 4 Million | Size and capacity
FIRE | Extinguisher-CO2 | 13105 |  | Statutory | Unique Bar Code | On Type Signage | 4 Million | Size and capacity
FIRE | Extinguisher-Vapourizing Liq | 13106 |  | Statutory | Unique Bar Code | On Type Signage | 4 Million | Size and capacity
FIRE | Extinguisher-Non Recharge | 13107 |  | Statutory | Unique Bar Code | On Type Signage | 4 Million | Size and capacity
FIRE | Extinguisher-Aerosol | 13108 |  | Statutory | Unique Bar Code | On Type Signage | 4 Million | Size and capacity
FIRE | Extinguisher-Wheeled | 13109 |  | Statutory | Unique Bar Code | On Type Signage | 4 Million | Size and capacity
FIRE | Fire Blanket | 13200 |  | Statutory | Unique Bar Code | On Type Signage | 4 Million | Size
FIRE | Passive-Barrier-Wall | 13401 |  | Statutory | Virtual Bar Code |  |  | Material of construction
FIRE | Passive-Barrier-Floor | 13402 |  | Statutory | Virtual Bar Code |  |  | Material of construction
FIRE | Passive-Barrier-Ceiling | 13403 |  | Statutory | Virtual Bar Code |  |  | Material of construction
FIRE | Passive-Barrier-Bulkhead | 13404 |  | Statutory | Virtual Bar Code |  |  | Material of construction
FIRE | Passive-Beam/Column/Truss | 13405 |  | Statutory | Virtual Bar Code |  |  | Material of construction
FIRE | Passive-Fire Door-Hinged | 13406 |  | Statutory | Unique Bar Code | Adjacent Door Tag | 4 Million | Size, FRL, hardware, site labelling name, asbestos
FIRE | Passive-Fire Door-Sliding | 13407 |  | Statutory | Unique Bar Code | Adjacent Door Tag | 4 Million | Size, FRL, hardware, site labelling name, asbestos
FIRE | Passive-Smoke Door-Hinged | 13408 |  | Statutory | Unique Bar Code | Adjacent Door Tag | 4 Million | Size, FRL, hardware, site labelling name, asbestos
FIRE | Passive Fire-Fire Shutter | 13409 |  | Statutory | Unique Bar Code | Adjacent Door Tag | 4 Million | Size, FRL, hardware, site labelling name, asbestos
FIRE | Passive-Glazing | 13410 |  | Statutory | Virtual Bar Code |  |  | Material of construction
FIRE | Passive-Access Panels | 13411 |  | Statutory | Virtual Bar Code |  |  | Material of construction
FIRE | Passive-Ceiling Hatches | 13412 |  | Statutory | Virtual Bar Code |  |  | Material of construction
FIRE | Passive-Ducts | 13413 |  | Statutory | Virtual Bar Code |  |  | Material of construction
FIRE | Passive-Stopping-Damper Seal | 13414 |  | Statutory | Virtual Bar Code |  |  | Material of construction
FIRE | Passive-Stopping-Penetration | 13415 |  | Statutory | Unique Bar Code | Adjacent site label | 4 Million | Site labelling number
FIRE | Passive-Stopping-Cntrl Joints | 13416 |  | Statutory | Virtual Bar Code |  |  | Material of construction
FIRE | Passive-Solid Core Doors | 13417 |  | Statutory | Unique Bar Code | Door Jamb | 4 Million | Size, FRL, hardware, site labelling name, asbestos
FIRE | Passive - Fire Curtain | 13418 |  | Statutory | Unique Bar Code | On Control Panel | 4 Million | Size, FRL, controller location
FIRE | Passive - Smoke Curtain | 13419 |  | Statutory | Unique Bar Code | On Control Panel | 4 Million | Size, FRL, controller location
FIRE | Passive - Double Fire Door | 13420 |  | Statutory | Unique Bar Code | Adjacent Door Tag | 4 Million | Size, FRL, hardware, site labelling name, asbestos
FIRE | Passive - Double Smoke Door | 13421 |  | Statutory | Unique Bar Code | Adjacent Door Tag | 4 Million | Size, FRL, hardware, site labelling name, asbestos
FIRE | Fire / Smoke Damper | 13503 |  | Statutory | Unique Bar Code | On Access Panel | 4 Million | Site labelling number
FIRE | A/C Fire Trip-Automatic Shutdown | 13506 |  | Statutory | Virtual Bar Code |  |  | Confirm if manual reset
FIRE | Egress-Power Operated Exit Doors | 13601 |  | Statutory | Unique Bar Code | On Controller | 4 Million | Size, material and driver capacity
FIRE | Egress-Exit/Egress Doors | 13602 |  | Statutory | Unique Bar Code | Door Jamb | 4 Million | Size
FIRE | Egress-Security Door Interface | 13603 |  | Statutory | Unique Bar Code | On Door Hardware | 4 Million | Door controller site labelling name
FIRE | Egress-Paths of Travel to Exits & Exit Stairs | 13604 |  | Statutory | Virtual Bar Code
FIRE | Egress-Evacuation Plans | 13605 |  | Statutory | Unique Bar Code | On Frame | 4 Million | Date installed
FIRE | Signage-Fire, Smoke & Egress Door Signage | 13701 |  | Statutory | Virtual Bar Code
FIRE | Signage-Fire Safety Notice | 13702 |  | Statutory | Virtual Bar Code
FUME CUPBOARD | Fume Cupboard Standard | 11311 |  | Statutory | Unique Bar Code | On Front Of Panel | 2 Million | Site labelling name
FUME CUPBOARD | Fume Cupboard Perchloric Acid | 11312 |  | Statutory | Unique Bar Code | On Front Of Panel | 2 Million | Site labelling name
FUME CUPBOARD | Fume Cupboard Hydrofluoric Acid | 11313 |  | Statutory | Unique Bar Code | On Front Of Panel | 2 Million | Site labelling name
FUME CUPBOARD | Fume Cupboard Recirculated Type | 11314 |  | Statutory | Unique Bar Code | On Front Of Panel | 2 Million | Site labelling name
FUME CUPBOARD | Fume Cupboard Fan | 11315 |  | Statutory | Unique Bar Code | On Front Of Panel | 2 Million | Site labelling name
FUME CUPBOARD | Fume Cupboard VSD | 11316 |  | Statutory | Unique Bar Code | On Front Of Panel | 2 Million | Site labelling name
FUME CUPBOARD | Fume Cupboard Scrubber | 11318 |  | Statutory | Unique Bar Code | On Side Of Unit | 2 Million | Site labelling name
GROUNDS | Fixed Barbeque (BBQ) | 33127 |  | Non-Statutory | Unique Bar Code | On Control Panel | 5 Million | Electric or gas
GROUNDS | External Paving | 45001 |  | Non-Statutory | Count/Building |  |  | Area (m2) and type
GROUNDS | Roads | 45002 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2) and materials
GROUNDS | Driveways | 45003 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2) and materials
GROUNDS | Pavements | 45004 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2) and materials
GROUNDS | Footpaths | 45005 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2) and materials
GROUNDS | External Bike Rack | 45051 |  | Non-Statutory | Virtual Bar Code |  |  | Number of racks
GROUNDS | External Furniture | 45052 |  | Non-Statutory | Virtual Bar Code |  |  | Type and materials
GROUNDS | External Bins | 45053 |  | Non-Statutory | Virtual Bar Code |  |  | Litres and type
GROUNDS | Bollards | 45054 |  | Non-Statutory | Virtual Bar Code |  |  | Removable or fixed
GROUNDS | Irrigation Controller | 45101 |  | Non-Statutory | Unique Bar Code | On Control Panel | 5 Million | Area (m2) served and location
GROUNDS | Trees | 45201 |  | Non-Statutory | Virtual Bar Code |  |  | Tree database number
GROUNDS | Lawns | 45202 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2)
GROUNDS | Garden Beds | 45203 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2)
GROUNDS | Planter Boxes | 45204 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2)
GROUNDS | Sporting Fields | 45205 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2)
GROUNDS | Decks | 45301 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2)
GROUNDS | Boardwalks | 45302 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2)
GROUNDS | Signs | 45401 |  | Non-Statutory | Virtual Bar Code |  |  | Type and materials
ICT AV | Wall Mounted Display Panel | 50001 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 1 Million
ICT AV | Interactive LCD | 50002 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 1 Million
ICT AV | USB Camera | 50003 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 1 Million
ICT AV | Document Camera | 50004 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 1 Million
ICT AV | Recording Camera and Mount | 50005 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 1 Million
ICT AV | Audio Amplifier | 50006 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 1 Million
ICT AV | Microphone | 50007 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 1 Million | Type
ICT AV | Lecturn | 50008 |  | Non-Statutory | Unique Bar Code | Adjacent nameplate | 1 Million
ICT AV | Hearing Loop | 50009 |  | Non-Statutory | Unique Bar Code | Adjacent Signage | 1 Million
ICT AV | IR Hearing Augmentation System | 50010 |  | Non-Statutory | Unique Bar Code | Adjacent Signage | 1 Million
ICT AV | ICT Projector | 50011 |  | Non-Statutory | Unique Bar Code | On Control Panel | 1 Million | [24 empty] | Water cooled Reciprocating Chiller
ICT AV | ICT Projector Screen | 50012 |  | Non-Statutory | Count/Room |  |  | Size | [23 empty] | Water Cooled Screw Chiller
INTERIORS | Blinds - Motorised | 33228 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Blinds - Manual | 33229 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Manual Operable Shading Louvre | 33243 |  | Non-Statutory | Count/Room |  |  | Area (m2)
INTERIORS | Automated Operable Shading Louvre | 33244 |  | Non-Statutory | Count/Room |  |  | Area (m2)
INTERIORS | Internal Handrails | 44001 |  | Non-Statutory | Count/Building |  |  | Lineal metres
INTERIORS | Internal Balustrades | 44002 |  | Non-Statutory | Count/Building |  |  | Area (m2)
INTERIORS | Internal Glazing | 44004 |  | Non-Statutory | Count/Building |  |  | Area (m2)
INTERIORS | Internal Glazed Doors | 44005 |  | Non-Statutory | Unique Bar Code | Door Jamb | 1 Million | Size, hardware
INTERIORS | Timber Doors | 44006 |  | NRM | Unique Bar Code | Door Jamb | 1 Million | Size, hardware
INTERIORS | Internal Waterproof Membrane | 44009 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Joinery | 44010 |  | NRM | Count/Building
INTERIORS | Bathroom Partitions | 44011 |  | NRM | Count/Room |  |  | Number of stalls
INTERIORS | Suspended Ceilings | 44013 |  | NRM | Count/Room |  |  | Area (m2) and type
INTERIORS | Internal Painting | 44014 |  | NRM | Count/Building
INTERIORS | Operable Walls | 44015 |  | NRM | Unique Bar Code | Wall Jamb | 1 Million | Size, hardware
INTERIORS | Compactus | 44016 |  | NRM | Unique Bar Code | Adjacent Nameplate | 1 Million | Size
INTERIORS | Curtains | 44017 |  | NRM | Count/Room |  |  | Area (m2) and fixing type
INTERIORS | Stair Nosings | 44018 |  | NRM | Count/Room |  |  | No. Stairs, Lineal metres
INTERIORS | Tactile Indicators | 44019 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Entrance Mat | 44101 |  | NRM | Virtual Bar Code |  |  | Area (m2) and type
INTERIORS | Flooring Carpet | 44102 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Carpet Tiles | 44103 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Concrete | 44104 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Flake Polyurethane | 44105 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Malthoid | 44106 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Marble | 44107 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Moasonite | 44108 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Painted Concrete | 44109 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Paving | 44110 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Pebble | 44111 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Polished Concrete | 44112 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Rubber | 44113 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Sand | 44114 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Soil | 44115 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Tarket | 44116 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Terrazzo | 44117 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Tiles | 44118 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Timber | 44119 |  | NRM | Count/Room |  |  | Area (m2)
INTERIORS | Flooring Vinyl | 44120 |  | NRM | Count/Room |  |  | Area (m2)
LIFT | Signage-Warning Signage for Passenger Lifts | 13703 |  | Statutory | Virtual Bar Code
LIFT | Passenger Lift Motor Room Less (MRL) | 14420 |  | Statutory | Unique Bar Code | In Lift Car On Control Panel | 7 Million | Load capacity, number of floors
LIFT | Passenger Lift Hydraulic | 14421 |  | Statutory | Unique Bar Code | In Lift Car On Control Panel | 7 Million | Load capacity, number of floors
LIFT | Passenger Lift Traction | 14422 |  | Statutory | Unique Bar Code | In Lift Car On Control Panel | 7 Million | Load capacity, number of floors
LIFT | Dumb Waiter | 14424 |  | Statutory | Unique Bar Code | On Motor/Engine | 7 Million | Load capacity, number of floors
LIFT | Wheelchair Lift Platform | 14425 |  | Statutory | Unique Bar Code | Adjacent Control Panel | 7 Million | Control type
LIFT | Escalators | 14426 |  | Statutory | Unique Bar Code | Adjacent Control Panel | 7 Million | Load capacity, number of steps
LIFT | Lift motor | 14428 |  | Statutory | Unique Bar Code | On Motor/Engine | 7 Million | Load capacity, number of floors
LIFT | Wheelchair Lift Car | 14430 |  | Statutory | Unique Bar Code | In Lift Car On Control Panel | 7 Million | Load capacity, number of floors
LOCKSMITH | Bilock General | 27250 |  | Non-Statutory | Count/Building |  |  | Quantity per building
LOCKSMITH | Bilock Campus | 27501 |  | Non-Statutory | Count/Building |  |  | Quantity per building
LOCKSMITH | Safe | 27600 |  | Non-Statutory | Unique Bar Code | Adjacent door handle | 8 Million
MECHANICAL | Air and Dirt Separator | 11409 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million
MECHANICAL | Air Conditioning Unit - Air Cooled Packaged Ducted | 11107 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Air Conditioning Unit - Air Cooled Split Condenser | 11103 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Air Conditioning Unit - Air Cooled Split FCU Ducted | 11105 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Air Conditioning Unit - Air Cooled Split indoor | 11104 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Air Conditioning Unit - Portable | 11102 |  | NRM | Unique Bar Code | Adjacent Nameplate | 2 Million
MECHANICAL | Air Conditioning Unit - Room Window or Wall-mounted | 11101 |  | NRM | Unique Bar Code | Adjacent Nameplate | 2 Million
MECHANICAL | Air Conditioning Unit - Water Cooled Ducted Package Unit | 11112 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Air Conditioning Unit - Water Cooled Floor Console Unit | 11111 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Air Conditioning Unit - Water Cooled Split Condenser | 11113 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Air Conditioning Unit - Water Cooled Split FCU Duc | 11115 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Air Conditioning Unit - Water Cooled Split indoor | 11114 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Air Cooled Reciprocating Chiller | 11427 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Air Cooled Screw Chiller | 11421 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Air Cooled Scroll Chiller | 11425 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Air Curtain | 11274 |  | NRM | Unique Bar Code | On Side Of Unit | 2 Million | Site labelling name
MECHANICAL | Air Filter - Absolute | 11224 |  | Non-Statutory | Unique Bar Code/Bank | On Filter Housing Access Panel |  | Filter size, numbers and air delivery type (SA/RA/OA)
MECHANICAL | Air Filter - Activated Carbon | 11225 |  | Non-Statutory | Unique Bar Code/Bank | On Filter Housing Access Panel |  | Filter size, numbers and air delivery type (SA/RA/OA)
MECHANICAL | Air Filter - Auto Roll | 11226 |  | Non-Statutory | Unique Bar Code/Bank | On Filter Housing Access Panel |  | Filter size, numbers and air delivery type (SA/RA/OA)
MECHANICAL | Air Filter - Bag Throw Away | 11219 |  | Non-Statutory | Unique Bar Code/Bank | On Filter Housing Access Panel |  | Filter size, numbers and air delivery type (SA/RA/OA)
MECHANICAL | Air Filter - Deep Bed | 11223 |  | Non-Statutory | Unique Bar Code/Bank | On Filter Housing Access Panel |  | Filter size, numbers and air delivery type (SA/RA/OA)
MECHANICAL | Air Filter - Electrostatic | 11227 |  | Non-Statutory | Unique Bar Code/Bank | On Filter Housing Access Panel |  | Filter size, numbers and air delivery type (SA/RA/OA)
MECHANICAL | Air Filter - Grease | 11228 |  | Non-Statutory | Unique Bar Code/Bank | On Filter Housing Access Panel |  | Filter size, numbers and air delivery type (SA/RA/OA)
MECHANICAL | Air Filter - HEPA | 11220 |  | Non-Statutory | Unique Bar Code/Bank | On Filter Housing Access Panel |  | Filter size, numbers and air delivery type (SA/RA/OA)
MECHANICAL | Air Filter - Metal Frame Pleated | 11217 |  | Non-Statutory | Unique Bar Code/Bank | On Filter Housing Access Panel |  | Filter size, numbers and air delivery type (SA/RA/OA)
MECHANICAL | Air Filter - Metal Frame Washable | 11218 |  | Non-Statutory | Unique Bar Code/Bank | On Filter Housing Access Panel |  | Filter size, numbers and air delivery type (SA/RA/OA)
MECHANICAL | Air Filter - Panel Throw Away | 11222 |  | Non-Statutory | Unique Bar Code/Bank | On Filter Housing Access Panel |  | Filter size, numbers and air delivery type (SA/RA/OA)
MECHANICAL | Air Filter - Panel washable | 11221 |  | Non-Statutory | Unique Bar Code/Bank | On Filter Housing Access Panel |  | Filter size, numbers and air delivery type (SA/RA/OA)
MECHANICAL | Air Handling Unit | 11241 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Air Receiver | 11403 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million
MECHANICAL | Air Scrubber (non fume cabinet) | 11441 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Airflow Valve | 11440 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Autoclave - Electric (Fixed units only) | 11342 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Autoclave - Gas (Fixed units only) | 11341 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Autoclave - Steam (Fixed units only) | 11437 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Blow Down Tank - Steam | 11167 |  | Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 2 Million | Tank size
MECHANICAL | Boiler Hot Water Heating - Electric | 11151 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Boiler Hot Water Heating - Gas | 11152 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Boiler Steam - Electric | 11153 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Boiler Steam - Gas | 11154 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Calorifier | 11166 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Car Park C0 Sensor | 11434 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Chilled Beam - Active | 11245 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Chilled Beam - Passive | 11246 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Chilled water Storage Tank | 11435 |  | Non-Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 2 Million | Site labelling name
MECHANICAL | Chiller - Air Cooled Centrifugal | 11141 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Chiller - Water Cooled Centrifugal | 11142 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Compressed Air Air Dryer | 11404 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million
MECHANICAL | Compressor - Air | 11401 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name and pressure capacity
MECHANICAL | Compressor - Refrigeration (For remote compressors only) | 11286 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Compressor - Vacuum | 11402 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name and pressure capacity
MECHANICAL | Computer Room Air Conditioning Unit - Air Cooled | 11108 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Computer Room Air Conditioning Unit - Water Cooled | 11116 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Condensate Pump | 11127 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Condenser Pump - Primary or Secondary | 11188 |  | Non-Statutory | Unique Bar Code | On Motor/Engine | 2 Million | Site labelling name
MECHANICAL | Condensing Unit Cool Room - Water-Cooled | 11324 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Condensing Unit Coolroom Room - Air Cooled | 11323 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Condensing Unit Environmental Control Room - Air C | 11331 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Condensing Unit Environmental Control Room - Water | 11332 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Condensing Unit Freezer Room - Air Cooled | 11327 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Condensing Unit Freezer Room - Water-Cooled | 11328 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Control - Pneumatic System | 11376 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Control Sensor - Gas | 11370 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Control Sensor - Humidity | 11366 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Control Sensor - PIR | 11371 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Control Sensor - Pressure | 11367 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Control Sensor - Temperature | 11365 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Control Sensor - Velocity | 11369 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Cooling Tower - Closed Loop | 11182 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Cooling Tower - Open | 11181 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Cooling tower - Sand Filter | 11186 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million
MECHANICAL | Coolroom | 11321 |  | Non-Statutory | Unique Bar Code | On Front Of Panel | 2 Million | Site labelling name
MECHANICAL | Damper - Balancing | 11233 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Damper - General | 11237 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Damper - Motorised | 11236 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Damper - Relief Air | 11234 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Damper - Spilled Air | 11235 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Dehumidifier - DX | 11277 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Dehumidifier - Elec | 11278 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Dehumidifier - Gas | 11276 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Duct Heater - Electric | 11265 |  | Statutory | Unique Bar Code | On Access Panel | 2 Million | Site labelling name
MECHANICAL | Ducted Gas Heater or Furnace for HVAC System | 11288 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Dust Extraction Unit | 11273 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Electric Humidifier | 11275 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Environmental Control Room | 11329 |  | Non-Statutory | Unique Bar Code | On Front Of Panel | 2 Million | Site labelling name
MECHANICAL | Evaporative Cooler | 11271 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Evaporator - Coolroom | 11322 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Evaporator - Environmental Control Room | 11330 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Evaporator - Freezer Room | 11326 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Expansion Tank Chilled Water - Gravity | 11136 |  | Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 2 Million | Site labelling name and size
MECHANICAL | Expansion Tank Chilled Water - Pressurised | 11137 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name and size
MECHANICAL | Expansion Tank Hot Water - Gravity | 11168 |  | Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 2 Million | Tank size
MECHANICAL | Expansion Tank Hot Water - Pressurised | 11169 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Tank size
MECHANICAL | Extraction Arm | 11439 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Fan Coil Unit - Ducted. Chilled, Hot Water or Electric Heating | 11243 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Fan Coil Unit - Gas Heating | 11244 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Fan Coil Unit - Non Ducted. Chilled, Hot Water or Electric Heating | 11242 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Fan Exhaust Air | 11205 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Fan Filter Unit | 11447 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Fan Pressurisation | 11206 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Fan Relief Air | 11203 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Fan Return Air | 11202 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Fan Roof-Mounted - Exhaust | 11210 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Fan Roof-Mounted - Supply | 11209 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Fan Smoke Spill | 11207 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Fan Spilled Air | 11204 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Fan Supply Air | 11201 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Fan Window or Wall-Mounted - Supply or Exhaust Air | 11208 |  | NRM | Unique Bar Code | On Side Of Unit | 2 Million | Site labelling name
MECHANICAL | Freezer Room | 11325 |  | Non-Statutory | Unique Bar Code | On Entry Door | 2 Million | Site labelling name
MECHANICAL | Gas Humidifier | 11446 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Heat Exchanger - Air To Air | 11281 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Heat Exchanger - Plate | 11279 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Heat Exchanger - Shell & Tube | 11280 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Heater - Gas Convection | 11303 |  | Non-Statutory | Unique Bar Code | Adjacent Valve | 2 Million | Site labelling name
MECHANICAL | Heater - Gas Radiant | 11304 |  | Non-Statutory | Unique Bar Code | Adjacent Valve | 2 Million | Site labelling name
MECHANICAL | HVAC UV light fixtures | 11433 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Size and number of tubes
MECHANICAL | Incinerator | 11272 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Inertia Tank - Chilled Water | 11140 |  | Non-Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 2 Million | Site labelling name and size
MECHANICAL | Inertia Tank - Hot Water | 11171 |  | Non-Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 2 Million | Site labelling name
MECHANICAL | Kitchen Exhaust Hood | 11283 |  | Statutory | Unique Bar Code | Adjacent Switch | 2 Million | Site labelling name
MECHANICAL | Kitchen Exhuast Fan | 11432 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Mechanical Services Control Panel | 11362 |  | Non-Statutory | Unique Bar Code | On Front Of Panel | 2 Million | Site labelling name
MECHANICAL | Mechanical Services Switchboard | 11361 |  | Non-Statutory | Unique Bar Code | On Front Of Panel | 2 Million | Site labelling name
MECHANICAL | Pump Chilled Water - Primary or Secondary | 11133 |  | Non-Statutory | Unique Bar Code | On Motor/Engine | 2 Million | Site labelling name
MECHANICAL | Pump Heating Water - Primary or Secondary | 11157 |  | Non-Statutory | Unique Bar Code | On Motor/Engine | 2 Million | Site labelling name
MECHANICAL | Refrigerant Detection Unit | 11139 |  | Non-Statutory | Unique Bar Code | On Front Of Panel | 2 Million
MECHANICAL | Sensible Cooling Coil | 11448 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Smoke & Heat Vents | 13507 |  | Non-Statutory | Unique Bar Code | Adjacent Manual Control Switch | 2 Million | Size and capacity
MECHANICAL | Smoke Control-Zone Pressurisation System | 13508 |  | Non-Statutory | Virtual Bar Code |  |  | System type
MECHANICAL | Special Exhaust Hood | 11284 |  | Non-Statutory | Unique Bar Code | Adjacent Switch | 2 Million | Site labelling name
MECHANICAL | Stair Pressurisation Fan | 11445 |  | Statutory | Unique Bar Code | On Front Of Panel | 2 Million | Site labelling name
MECHANICAL | Steam Trap | 11165 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | Supply / Exhuast Air Valve | 11436 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million
MECHANICAL | Thermal Ceiling Diffuser | 11248 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | VAV Box | 11247 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Ventilated Cabinet/Workbench | 11443 |  | Non-Statutory | Unique Bar Code | On Front Of Panel | 2 Million | Site labelling name
MECHANICAL | VRV Air Cooled Condenser | 11121 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | VRV Air Cooled Gas Driven Condenser | 11429 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | VRV Branch Control Unit | 11123 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | VRV Control Panel | 11124 |  | Non-Statutory | Virtual Bar Code
MECHANICAL | VRV Split FCU Ducted | 11126 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | VRV Split indoor single FCU | 11125 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | VRV Water Cooled Condenser | 11122 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | VRV Water Cooled Gas Driven Condenser | 11430 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | VSD | 11428 |  | Non-Statutory | Unique Bar Code | On Front Of Panel | 2 Million | Site labelling name
MECHANICAL | Water Cooled Gas Driven Screw Chiller | 11423 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Water cooled Reciprocating Chiller | 11426 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Water Cooled Screw Chiller | 11422 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Water cooled Scroll Chiller | 11424 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
MECHANICAL | Wind Powered Roof Ventilator | 11211 |  | Non-Statutory | Unique Bar Code | On Side Of Unit | 2 Million | Site labelling name
MEDICAL AND LAB GASSES | Medical and Lab Gas Monitor/Panel | 11442 |  | Statutory | Unique Bar Code | On Front Of Panel | 9 Million | Site labelling name
MEDICAL AND LAB GASSES | Medical and Laboratory Gas Valve Set | 11444 |  | Non-Statutory | Unique Bar Code | Adjacent Valve | 9 Million | Site labelling name
MEDICAL AND LAB GASSES | Speciality Gas Cabinet | 33160 |  | Statutory | Unique Bar Code | On Door | 9 Million | Size and capacity
MEDICAL AND LAB GASSES | Bulk Gas - Carbon Dioxide | 47001 |  | Non-Statutory | Unique Bar Code | On Manifold | 9 Million | Size and capacity
MEDICAL AND LAB GASSES | Bulk Gas - Nitrogen | 47002 |  | Non-Statutory | Unique Bar Code | On Manifold | 9 Million | Size and capacity
MEDICAL AND LAB GASSES | Bulk Gas - High Purity Nitrogen | 47003 |  | Non-Statutory | Unique Bar Code | On Manifold | 9 Million | Size and capacity
MEDICAL AND LAB GASSES | Bulk Gas - Argon | 47004 |  | Non-Statutory | Unique Bar Code | On Manifold | 9 Million | Size and capacity
MEDICAL AND LAB GASSES | Liquid Nitrogen Tank | 47005 |  | Non-Statutory | Unique Bar Code | On Manifold | 9 Million | Size and capacity
MEDICAL AND LAB GASSES | Liquid Nitrogen Dewar | 47006 |  | Non-Statutory | Unique Bar Code | On Manifold | 9 Million | Size and capacity
MEDICAL AND LAB GASSES | Medical Oxygen | 47007 |  | Non-Statutory | Unique Bar Code | On Manifold | 9 Million | Size and capacity
MEDICAL AND LAB GASSES | Medical Nitous Oxde | 47008 |  | Non-Statutory | Unique Bar Code | On Manifold | 9 Million | Size and capacity
MEDICAL AND LAB GASSES | Medical Air | 47009 |  | Non-Statutory | Unique Bar Code | On Manifold | 9 Million | Size and capacity
MEDICAL AND LAB GASSES | Gas Sensor - Oxygen Depletion | 47051 |  | Statutory | Unique Bar Code | Adjacent Sensor | 9 Million | Site labelling name
MEDICAL AND LAB GASSES | Gas Sensor - Crabon Dioxide | 47052 |  | Statutory | Unique Bar Code | Adjacent Sensor | 9 Million | Site labelling name
MEDICAL AND LAB GASSES | Gas Sensor - LEL | 47053 |  | Statutory | Unique Bar Code | Adjacent Sensor | 9 Million | Site labelling name
PLUMBING | Fountain | 11287 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2)
PLUMBING | Reverse Osmosis Unit | 11294 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 5 Million | Site labelling name
PLUMBING | Water Purification Unit | 11295 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 5 Million | Site labelling name
PLUMBING | Potable Water Storage Tank | 16000 |  | Non-Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 5 Million | Tank size
PLUMBING | Non Potable Lab Water Storage Tank | 16001 |  | Non-Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 5 Million | Tank size
PLUMBING | Rain Water Storage Tank | 16002 |  | Non-Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 5 Million | Tank size
PLUMBING | Flusherette Tank | 16003 |  | Non-Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 5 Million | Tank size
PLUMBING | Expansion Tank | 16004 |  | Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 5 Million | Tank size
PLUMBING | Solar Panels Hot water | 16010 |  | Non-Statutory | Unique Bar Code | On Frame Near Pipe Entry | 5 Million | Size and output
PLUMBING | Solar Panels Storage Tank | 16011 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 5 Million | Tank size
PLUMBING | Submersible Pump | 16020 |  | Non-Statutory | Unique Bar Code | On Control Panel | 5 Million | Motor capacity
PLUMBING | Hot Water Pump (Recirculating) | 16021 |  | Non-Statutory | Unique Bar Code | On Motor/Engine | 5 Million | Motor capacity
PLUMBING | Cold Water Pump | 16022 |  | Non-Statutory | Unique Bar Code | On Motor/Engine | 5 Million | Motor capacity
PLUMBING | Water Filter - Cartridge Type | 16031 |  | Non-Statutory | Unique Bar Code | Adjacent Housing | 5 Million | Size and type
PLUMBING | Water Filter - UV | 16032 |  | Non-Statutory | Unique Bar Code | Adjacent Housing | 5 Million | Size and number of tubes
PLUMBING | Water Filter - Automatic Backwash | 16033 |  | Non-Statutory | Unique Bar Code | Adjacent Housing | 5 Million | Size and type
PLUMBING | Subsoil Filter - Bag | 16034 |  | Non-Statutory | Unique Bar Code | Adjacent Housing | 5 Million | Size and type
PLUMBING | Rainwater Filter - First Flush | 16035 |  | Non-Statutory | Unique Bar Code | Adjacent Housing | 5 Million
PLUMBING | Natural Gas Regulator | 16042 |  | NRM | Unique Bar Code | On Equipment | 5 Million | Pressure input and output
PLUMBING | Natural Gas Double Outlet | 16043 |  | NRM | Virtual Bar Code
PLUMBING | Natural Gas Single Outlet | 16044 |  | NRM | Virtual Bar Code
PLUMBING | Natural Gas Flue | 16047 |  | Non-Statutory | Virtual Bar Code
PLUMBING | Natural Gas Shut Off Valve | 16048 |  | Non-Statutory | Unique Bar Code | Adjacent Valve | 5 Million | Manual or automatic and systems type
PLUMBING | Sewer Pit | 16051 |  | NRM | Virtual Bar Code
PLUMBING | Sewerage Treatment Plant | 16060 |  | Non-Statutory | Unique Bar Code | On Control Panel | 5 Million | System details including holding tanks, pumps, etc
PLUMBING | Sewer Pump | 16061 |  | Non-Statutory | Unique Bar Code | On Control Panel | 5 Million | Motor capacity
PLUMBING | Reflux Valve | 16062 |  | NRM | Virtual Bar Code
PLUMBING | Grease Trap | 16063 |  | Statutory | Unique Bar Code | Use Sydney Water Barcode | 5 Million | Size and Sydney Water trade waste permit number
PLUMBING | Envirocycle Sewerage System | 16064 |  | Non-Statutory | Unique Bar Code | On Control Panel | 5 Million | System details including holding tanks, pumps, etc
PLUMBING | WC Pan - General | 16070 |  | NRM | Virtual Bar Code
PLUMBING | Urinal | 16071 |  | NRM | Virtual Bar Code
PLUMBING | Bath | 16073 |  | NRM | Virtual Bar Code
PLUMBING | Shower General | 16074 |  | NRM | Virtual Bar Code
PLUMBING | Urinal Waterless | 16075 |  | Non-Statutory | Virtual Bar Code
PLUMBING | Urinal Flush Sensor | 16076 |  | NRM | Unique Bar Code | Adjacent Sensor | 5 Million | Battery or mains powered
PLUMBING | Sink Kitchen | 16080 |  | NRM | Virtual Bar Code
PLUMBING | Sink Lab | 16081 |  | NRM | Virtual Bar Code
PLUMBING | Sink Cleaner | 16082 |  | NRM | Virtual Bar Code
PLUMBING | Laundry Sink | 16083 |  | NRM | Virtual Bar Code
PLUMBING | Hand Basin - General | 16084 |  | NRM | Virtual Bar Code
PLUMBING | Hand Basin - Accessible | 16085 |  | NRM | Virtual Bar Code
PLUMBING | Taps General | 16090 |  | NRM | Virtual Bar Code
PLUMBING | Taps Lab | 16091 |  | NRM | Virtual Bar Code
PLUMBING | Hose Tap | 16092 |  | NRM | Virtual Bar Code
PLUMBING | Boiling Water Unit | 16100 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 5 Million | Tap type
PLUMBING | Boiling & Chilled Water Unit | 16101 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 5 Million | Tap type
PLUMBING | HWU Electric | 16110 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 5 Million | Size and capacity
PLUMBING | HWU Gas | 16111 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 5 Million | Size and capacity
PLUMBING | Hot Water - Heat Exchanger | 16112 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 5 Million
PLUMBING | Hot Water Storage Tank | 16117 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 5 Million | Tank size
PLUMBING | Control Valve Gas | 16120 |  | NRM | Virtual Bar Code
PLUMBING | Control Valve Water | 16121 |  | NRM | Virtual Bar Code
PLUMBING | Backflow Prevention Device | 16130 |  | Statutory | Unique Bar Code | On Valve Tag Or Housing | 5 Million | Containment type (site/zone/individual) and hazard rating
PLUMBING | Emergency Safety Shower | 16131 |  | Statutory | Unique Bar Code | On Signage | 5 Million
PLUMBING | Emergency Eye Wash Facility | 16132 |  | Statutory | Unique Bar Code | On Signage | 5 Million
PLUMBING | Thermostatic Mixing Valve | 16133 |  | Statutory | Unique Bar Code | On Valve Tag Or Housing | 5 Million | Number fixtures served
PLUMBING | Tempering Valve | 16134 |  | Statutory | Unique Bar Code | On Valve Tag Or Housing | 5 Million | Number fixtures served
PLUMBING | Access Chamber | 16171 |  | NRM | Virtual Bar Code
PLUMBING | Boundary Trap | 16173 |  | NRM | Virtual Bar Code
PLUMBING | Greywater Treatment System | 16179 |  | Non-Statutory | Unique Bar Code | On Control Panel | 5 Million | System details including holding tanks, pumps, etc
PLUMBING | Waste Oil Tank | 16191 |  | Non-Statutory | Unique Bar Code | On Side Of Tank Adjacent Signage | 5 Million | Tank size
PLUMBING | Air Admittance Valve | 16202 |  | NRM | Virtual Bar Code
PLUMBING | Boundary Valve | 16211 |  | NRM | Virtual Bar Code
PLUMBING | Boundary Valve With PRV | 16212 |  | NRM | Virtual Bar Code |  |  | Pressure setting
PLUMBING | Storm Water Grated Drain | 16217 |  | Non-Statutory | Virtual Bar Code
PLUMBING | Water Meter | 16240 |  | Non-Statutory | Unique Bar Code | On Valve Tag Or Housing | 5 Million | AUMS device number, ownership
PLUMBING | Gas Meter | 16241 |  | Non-Statutory | Unique Bar Code | On Valve Tag Or Housing | 5 Million | AUMS device number, ownership
PLUMBING | External Fountain Drinking | 16250 |  | Non-Statutory | Unique Bar Code | Adjacent Nameplate | 5 Million | Filter details
PLUMBING | Water Filter Bag Type | 16301 |  | Non-Statutory | Unique Bar Code | Adjacent Housing | 5 Million | Size and type
PLUMBING | WC Pan - Ambulatory | 16302 |  | NRM | Virtual Bar Code
PLUMBING | WC Pan - Accessible | 16303 |  | NRM | Virtual Bar Code
PLUMBING | Accessible Shower | 16304 |  | NRM | Virtual Bar Code
PLUMBING | Hand Basin - Lab | 16305 |  | NRM | Virtual Bar Code
PLUMBING | Storm Water Pit | 16306 |  | NRM | Virtual Bar Code |  |  | Size
PLUMBING | Trade Waste Cooling Pit | 16307 |  | Non-Statutory | Virtual Bar Code |  |  | Size and Sydney Water trade waste permit number
PLUMBING | Gross Pollutant Trap | 16308 |  | Non-Statutory | Virtual Bar Code |  |  | Size
PLUMBING | Trade Waste Dilution Pit | 16309 |  | Non-Statutory | Virtual Bar Code |  |  | Size and Sydney Water trade waste permit number
PLUMBING | Trade Waste General Purpose Trap Pit | 16310 |  | Non-Statutory | Virtual Bar Code |  |  | Size and Sydney Water trade waste permit number
PLUMBING | Silt Arrestor | 16311 |  | Non-Statutory | Virtual Bar Code |  |  | Size and Sydney Water trade waste permit number
PLUMBING | Dry Basket Arrestor | 16312 |  | Non-Statutory | Virtual Bar Code |  |  | Size and Sydney Water trade waste permit number
PLUMBING | On Site Detention Tank | 16313 |  | Non-Statutory | Virtual Bar Code |  |  | Tank size
PLUMBING | Urinal Trough Type | 16314 |  | NRM | Virtual Bar Code |  |  | Lineal metres
PLUMBING | Storm Water Pump | 16315 |  | Non-Statutory | Unique Bar Code | On Control Panel | 5 Million | Motor capacity
PLUMBING | Sensor Taps | 16316 |  | NRM | Virtual Bar Code |  |  | Battery or mains powered
PLUMBING | Decorative Fountain | 16317 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2)
PLUMBING | Decorative Fountain Pump | 16318 |  | Non-Statutory | Unique Bar Code | On Control Panel | 5 Million | Motor capacity
PLUMBING | Waste Water Treatment Plant | 16319 |  | Non-Statutory | Unique Bar Code | On Control Panel | 5 Million | System details including holding tanks, pumps, etc
PLUMBING | Rain Water Treatment Plant | 16320 |  | Non-Statutory | Unique Bar Code | On Control Panel | 5 Million | System details including holding tanks, pumps, etc
PLUMBING | Cleaners Tap | 33299 |  | NRM | Virtual Bar Code
PLUMBING | Hose Cock | 33300 |  | NRM | Virtual Bar Code
RELAMPING & LIGHTING | Seat Light | 14206 |  | Non-Statutory | Virtual Bar Code |  |  | Lamp type and size
RELAMPING & LIGHTING | Step Light | 14207 |  | Non-Statutory | Virtual Bar Code |  |  | Lamp type and size
RELAMPING & LIGHTING | Isle Light | 14208 |  | Non-Statutory | Virtual Bar Code |  |  | Lamp type and size
RELAMPING & LIGHTING | Heritage Feature Light | 14265 |  | NRM | Virtual Bar Code |  |  | Lamp type and size
RELAMPING & LIGHTING | Modern Feature Light | 14266 |  | NRM | Virtual Bar Code |  |  | Lamp type and size
RELAMPING & LIGHTING | T5 Single | 14500 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | T5 Twin | 14501 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | T5 Triple | 14502 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | T8 Single | 14503 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | T8 Twin | 14504 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | T8 Triple | 14505 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | T12 Single | 14506 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | T12 Twin | 14507 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | T12 Triple | 14508 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | Incandescent Globe Light | 14509 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | Linear Led Tube/Strip Single | 14510 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | Linear Led Tube/Strip Twin | 14511 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | Downlight MR16, Dichroic Halogen Lamp | 14512 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | Downlight Compact Fluorescent CFL/PLC Single Lamp | 14513 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | Downlight Compact Fluorescent CFL/PLC Twin Lamps | 14514 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | Downlight Parabolic Aluminised Reflector PAR Halogen Lamp | 14515 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | Downlight LED Lamp | 14516 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | High/Low Bay Mecury Vapour Light | 14517 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | High/Low Bay Metal Halide Light | 14518 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | High/Low Bay Fluorescent Light | 14519 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | High/Low Bay LED Light | 14520 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | High/Low Bay induction Lamp | 14521 |  | NRM | Count/Room |  |  | Lamp type and size
RELAMPING & LIGHTING | Exterior Halogen Box Floodlights | 14522 |  | Non-Statutory | Unique Bar Code | On Light Fitting | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Exterior Metal Halide Floodlight | 14523 |  | Non-Statutory | Unique Bar Code | On Light Fitting | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Exterior LED Floodlight | 14524 |  | Non-Statutory | Unique Bar Code | On Light Fitting | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Road/Path lighting Kim Bounce Pole Light <4M Metal Halide Lamp | 14525 |  | Non-Statutory | Unique Bar Code | On Light Post | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Road/Path lighting Kim Bounce Pole Light <4M LED Luminaire | 14526 |  | Non-Statutory | Unique Bar Code | On Light Post | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Road/Path lighting Kim Bounce Pole Light >4M Metal Halide Lamp | 14527 |  | Non-Statutory | Unique Bar Code | On Light Post | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Road/Path lighting Kim Bounce Pole Light >4M LED Luminaire | 14528 |  | Non-Statutory | Unique Bar Code | On Light Post | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Road/Path lighting Louis Polsen Pole Light <4m Metal Halide Lamp | 14529 |  | Non-Statutory | Unique Bar Code | On Light Post | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Road/Path lighting Louis Polsen Pole Light >4m Metal Halide Lamp | 14530 |  | Non-Statutory | Unique Bar Code | On Light Post | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Road/Path lighting Kim Archetype External Light Metal Halide Lamp | 14531 |  | Non-Statutory | Unique Bar Code | On Light Post | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Road/Path Mercury Vapour Street Light | 14532 |  | Non-Statutory | Unique Bar Code | On Light Post | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Road/Path Sodium Vapour Street Light | 14533 |  | Non-Statutory | Unique Bar Code | On Light Post | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Road/Path Fluorescent Vapour Street Light | 14534 |  | Non-Statutory | Unique Bar Code | On Light Post | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Road/Path Fluorescent LED Street Light | 14535 |  | Non-Statutory | Unique Bar Code | On Light Post | 3 Million | Lamp type and size
RELAMPING & LIGHTING | Occupancy Sensor PIR Type | 14548 |  | Non-Statutory | Count/Room
RELAMPING & LIGHTING | Occupancy Sensor Microwave Type | 14549 |  | Non-Statutory | Count/Room
RELAMPING & LIGHTING | Occupancy Sensor Ultrasonic Type | 14550 |  | Non-Statutory | Count/Room
RELAMPING & LIGHTING | Occupancy Sensor Hybrid Type | 14551 |  | Non-Statutory | Count/Room
RELAMPING & LIGHTING | Sports Field Flood Lighting | 14553 |  | Non-Statutory | Unique Bar Code | On Light Post | 3 Million | Lamp type and size
ROOF & GUTTER | Roof - Mixed Fabric | 16140 |  | Non-Statutory | Count/Building |  |  | Roof area (m2)
ROOF & GUTTER | Access Hatch | 16141 |  | Non-Statutory | Virtual Bar Code
ROOF & GUTTER | Slate Roof | 16142 |  | Non-Statutory | Count/Building |  |  | Roof area (m2)
ROOF & GUTTER | Copper Roof | 16143 |  | Non-Statutory | Count/Building |  |  | Roof area (m2)
ROOF & GUTTER | Tile Roof | 16144 |  | Non-Statutory | Count/Building |  |  | Roof area (m2)
ROOF & GUTTER | Metal Roof | 16145 |  | Non-Statutory | Count/Building |  |  | Roof area (m2)
ROOF & GUTTER | Concrete Roof | 16146 |  | Non-Statutory | Count/Building |  |  | Roof area (m2)
ROOF & GUTTER | Gutter/Downpipe | 16147 |  | Non-Statutory | Count/Building |  |  | Lineal metres
ROOF & GUTTER | Rain Water Head | 16148 |  | Non-Statutory | Count/Building |  |  | Quantity per building
ROOF & GUTTER | Box Gutter | 16149 |  | Non-Statutory | Count/Building |  |  | Lineal metres
ROOF & GUTTER | Valley/Ridge | 16150 |  | NRM | Count/Building |  |  | Lineal metres
ROOF & GUTTER | External Waterproof Membrane | 16151 |  | NRM | Count/Building |  |  | Roof area (m2)
ROOF SAFETY | Anchor Point | 16160 |  | Statutory | Virtual Bar Code
ROOF SAFETY | Static Lines | 16161 |  | Statutory | Virtual Bar Code |  |  | Lineal metres
ROOF SAFETY | Fall Arrest Barriers | 16162 |  | Statutory | Virtual Bar Code
ROOF SAFETY | Ladder Bracket | 16163 |  | Statutory | Virtual Bar Code |  |  | Height
ROOF SAFETY | Fixed Ladder | 16164 |  | Statutory | Virtual Bar Code |  |  | Number rungs
ROOF SAFETY | Walkway | 16165 |  | Statutory | Virtual Bar Code |  |  | Lineal metres
ROOF SAFETY | Access Platform | 16166 |  | Statutory | Virtual Bar Code |  |  | Size
ROOF SAFETY | Davit Arm | 16167 |  | Statutory | Unique Bar Code | On Base | 7 Million | Load capacity
SECURITY ELECTRONIC | DVR | 27012 |  | Statutory | Unique Bar Code | Adjacent equipment | 8 Million
SECURITY ELECTRONIC | CCTV Camera - Internal | 27018 |  | Statutory | Unique Bar Code | Adjacent equipment | 8 Million | Addressable device number
SECURITY ELECTRONIC | PSU | 27019 |  | Statutory | Unique Bar Code | Adjacent equipment | 8 Million | Number, type and size of batteries
SECURITY ELECTRONIC | Duress Button | 27022 |  | Statutory | Unique Bar Code | Adjacent equipment | 8 Million | Addressable device number
SECURITY ELECTRONIC | Glass Break Detector | 27023 |  | Non-Statutory | Unique Bar Code | Adjacent equipment | 8 Million | Addressable device number
SECURITY ELECTRONIC | Passive Infrared Sensor | 27032 |  | Non-Statutory | Unique Bar Code | Adjacent equipment | 8 Million | Addressable device number
SECURITY ELECTRONIC | Reed Switch | 27033 |  | Non-Statutory | Unique Bar Code | Adjacent equipment | 8 Million | Addressable device number
SECURITY ELECTRONIC | Security Temperature Alarm | 27039 |  | Non-Statutory | Virtual Bar Code |  |  | Addressable device number
SECURITY ELECTRONIC | Access Door | 27041 |  | Statutory | Unique Bar Code | Adjacent equipment | 8 Million | Addressable device number
SECURITY ELECTRONIC | Aperio Door | 27048 |  | Statutory | Unique Bar Code | Adjacent equipment | 8 Million
SECURITY ELECTRONIC | Electronic Security Controller | 27049 |  | Statutory | Unique Bar Code | Adjacent equipment | 8 Million | Addressable device number
SECURITY ELECTRONIC | Emergency Help Point | 27050 |  | Statutory | Unique Bar Code | Adjacent equipment | 8 Million | Addressable device number
SECURITY ELECTRONIC | Security Fire Trip Alarm | 27051 |  | Statutory | Virtual Bar Code |  |  | Addressable device number
SECURITY ELECTRONIC | Security Gas Alarm | 27052 |  | Non-Statutory | Virtual Bar Code |  |  | Addressable device number
SECURITY ELECTRONIC | Security BMS Alarm | 27053 |  | Non-Statutory | Virtual Bar Code |  |  | Addressable device number
SECURITY ELECTRONIC | Glass Furnace Alarm | 27054 |  | Non-Statutory | Virtual Bar Code |  |  | Addressable device number
SECURITY ELECTRONIC | Reciever | 27055 |  | Non-Statutory | Unique Bar Code | Adjacent equipment | 8 Million | Addressable device number
SECURITY ELECTRONIC | Remote Release | 27056 |  | Non-Statutory | Unique Bar Code | Adjacent equipment | 8 Million | Addressable device number
SECURITY ELECTRONIC | Secured Lifts | 27057 |  | Non-Statutory | Virtual Bar Code |  |  | Lift number, addressable device number
SECURITY ELECTRONIC | CCTV Camera - External | 27058 |  | Statutory | Unique Bar Code | Adjacent equipment | 8 Million | Addressable device number
STRUCTURE | Skylight | 42001 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2)
STRUCTURE | Awning | 42002 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2)
STRUCTURE | Shade Structures | 42003 |  | Non-Statutory | Virtual Bar Code |  |  | Area (m2)
STRUCTURE | Structural Steel | 42004 |  | Non-Statutory | Count/Building |  |  | Lineal metres
SUBSTRUCTURE | Footings | 40001 |  | NRM | Count/Building
SUBSTRUCTURE | Piled Wall | 40002 |  | NRM | Count/Building |  |  | Area (m2), Height
SUBSTRUCTURE | Retaining Wall | 40003 |  | NRM | Count/Building |  |  | Area (m2), Height
SUBSTRUCTURE | Termite Protection | 40004 |  | NRM | Count/Building |  |  | Area (m2)
SUBSTRUCTURE | Concrete Structure | 40005 |  | NRM | Count/Floor |  |  | Area (m2)
TRAFFIC | Carparking Payment Machine | 46001 |  | Non-Statutory | Virtual Bar Code |  |  | Site labelling name
TRAFFIC | Carparking Space | 46002 |  | Non-Statutory | Virtual Bar Code |  |  | Car park space number and type
WASTE | Bin Internal | 33153 |  | NRM | Virtual Bar Code |  |  | Size
WASTE | External Large Mobile Bin | 33154 |  | NRM | Virtual Bar Code |  |  | Size
WASTE | Public Space External Fixed Bin | 33155 |  | NRM | Virtual Bar Code |  |  | Size
WASTE | Garbage Bin - 50 litre | 33269 |  | NRM | Virtual Bar Code
WASTE | Garbage Bin - 15 litre | 33270 |  | NRM | Virtual Bar Code
WASTE | Garbage Bin - 25 litre | 33271 |  | NRM | Virtual Bar Code
WASTE | Wheelie Bin - 60 litre | 33272 |  | NRM | Virtual Bar Code
WASTE | Waste Bin - 135 litre | 33273 |  | NRM | Virtual Bar Code
WATER TREATMENT | Cooling Tower - Open | 11181 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
WATER TREATMENT | Cooling Tower - Closed Loop | 11182 |  | Statutory | Unique Bar Code | Adjacent Nameplate | 2 Million | Site labelling name
WATER TREATMENT | Pump Chemical Dosing | 11185 |  | Statutory | Unique Bar Code | On Motor | 2 Million
WATER TREATMENT | Water Treatment Sand Filter | 11187 |  | Statutory | Unique Bar Code | On Side Of Filter | 2 Million
WATER TREATMENT | Chemical Dosing Station (Automatic Dosing) | 11189 |  | Statutory | Unique Bar Code | On Front Of Panel | 2 Million
WATER TREATMENT | Chemical Dosing Pot Condenser loop | 11417 |  | Statutory | Unique Bar Code | On Side Of Pot | 2 Million
WATER TREATMENT | Chemical Dosing Pot Heating loop | 11418 |  | Statutory | Unique Bar Code | On Side Of Pot | 2 Million
WATER TREATMENT | Boiler Softener | 11450 |  | Non-Statutory | Unique Bar Code | On Side Of Pot | 2 Million

## 4 - Modifications (#)
Tab 4 - Asset Modifications - Used to define modification to the attributes of an existing asset | [25 empty] | Asset Assessment Section - Used when performing asset validation and condition assessments (refer to assessment tables tab)
Additional notes supporting details of information capture, validation, condition assessment (free text field) | Date Asset Information captured (DD/MM/YYYY). | Unique identifier from existing asset register, proposed to be modified (row copied from Tab 9 - Existing Asset Register) | Confirm any changes to existing unique identifier to meet requirements of Tab 3 - Master Equipment Standards, Option 1 column (ie, unique bar code asset, virtual asset, item count asset). Changes to existing equipment codes to be listed to ensure asset history is maintained for assets that had incorrect equipment codes or have newly assigned unique bar code. | Identifies the Equipment Code of the Parent of this Asset to create an asset hierarchy (ie, for a smoke detector the equipment code for the building FIP would be inserted). If the asset is the parent then copy equipment code in this field | Category, as per Tab 3 - Master Equipment Standards (select this value first from drop down) | Linked to Equipment Standard Category, as per Tab 3 - Master Equipment Standards (select this value after equipment standard category selection, from drop down) | Code linked to equipment standard description as per Tab 3 - Master Equipment Standard (auto generated based on Equipment Standard Category and Equipment Standard Description selections in previous columns) | Type linked to equipment standard description as per Tab 3 - Master Equipment Standard (auto generated based on Equipment Standard Category and Equipment Standard Description selections in previous columns) | Building Name - linked to Building Code (as per space data listing) | Building Code (as per space data listing) | Floor Code (as per space data listing) | Room Code (as per space data listing) | Location (concatenation of the building - floor - room for validation) Automatically generated | For GPS location of external assets (mandatory for all assets external to building rooms) | For GPS location of external assets (mandatory for all assets external to building rooms) | To identify location of Asset within the room (free text field) | Manufacturer of Equipment (free text field) | Model of Equipment (free text field) | Serial Number (free text field) | Estimated date asset was placed in service (DD/MM/YYYY). | Estimated operational life of the asset when originally placed in service (years) | If the asset has a known warranty, state duration (years) | Identifies status of asset as, per Tab 8 - Equipment Status Table (select this value from drop down) | Include all mandatory information, as per Tab 3 - Master Equipment Standards comments column, and any other information that may be useful (free text field) | Confirm photo reference number from folder containing photos of all assets. | Identifies condition of asset, as per Tab 7 - Assessment Tables (select this value from drop down) | Numerical Value (auto generated as per assessment tables tab) | Identifies criticality of asset, as per Tab 7 - Assessment Tables (select this value from drop down) | Numerical Value (auto generated as per assessment tables) | Identifies priority rating of asset, as per Tab 7 - Assessment Tables (select this value from drop down) | Numerical Value (auto generated to suit assessment tables) | Identifiesrecommended actions for asset, as per Tab 7 - Assessment Tables (select this value from drop down) | Numerical Value (auto generated to suit assessment tables) | Estimated cost to bring the Asset back to excellent working condition. ($) | Replacement Value at time of Assessment. ($) | Description of the condition of the Asset and any recommended repairs (free text field)
Notes | Date Information Captured | Existing Equipment Code | New Equipment Code | Subcomponent Of | Equipment Standard Category | Equipment Standard Description | Equipment Standard | Equipment Code Type | Building Name | Building Code | Floor Code | Room Code | Bulding - Floor - Room | Latitude | Longitude | Asset Location | Manufacturer | Model | Serial Number | In Service Date | Years Life Expectancy | Warranty | Equipment Status | Comments | Photo Ref Number | Condition Rating | Condition Rating (Number) | Criticality Rating | Criticality Rating (Number) | Priority Rating | Priority Rating (Number) | Recommended Action | Recommended Action (Number) | Repair Cost | Replacement Cost | Description
Examples | 2019-09-21 | A09-01-122-12108-01 | 4000978 | 4000978 | FIRE | EWIS Panel | 12108 | Statutory | Holme Building & Footbridge Theatre | A09 | 01 | 122 | A09-01-122 |  |  | Next to main entrance | Vigilant | QE90 | 0340504/508 | 2011-03-24 | 15 | 10 years | In Service | MNS device: 032-501 , battery number: 0010284 , size: 1.2m x 0.73m | A09-01-122-EWIS | Good | 2 | High Criticality | 4 | Facility Loss | 8 | Repair | 4 | 350 | 7500 | Minor issues with panel glass and housing
| 2019-09-21 | 2017842 |  | 2017842 | FUME CUPBOARD | Fume Cupboard Standard | 11311 | Statutory | Charles Perkins Centre | D17 | 05 | 5309 | D17-05-5309 |  |  | Along back wall, north-west corner | Dynaflow-GRP | FCM#1500 | FCM1500-0230-12 | 2013-07-01 | 20 |  | In Service | Site labelling name: Lab 5 Fume | D17-05-5309-Fume-02 | Poor | 4 | High Criticality | 4 | Mission Support | 6 | Replace | 5 | 18500 | 20000 | Solenoid broken, power adjustment
| 2019-09-21 | K25-B1-B128-14338-02 |  | 3000287 | ELECTRICAL | Generator Inlet | 14338 | Non-Statutory | Medical Foundation Building | K25 | B1 | B128 | K25-B1-B128 |  |  |  | Perkins | 28106CE16TAG2 | HGB061161 | 2006-01-01 | 30 | 1 Year | In Service | Generator inlet - 15amp 1phase captive inlet | K25-B1-B128-Generator-Inlet | Good | 2 | Extremely Critical | 5 | Mission Support | 6 | Clean | 1 | 123.5 | 2800 | Need cleaning of outer area
| 2019-09-21 | J13-02-246-14401-01 | J13-02-246-33230-01 | 3000548 | ELECTRICAL | Ceiling Fan\Light | 33230 | NRM | Engineering Link Building | J13 | 02 | 246 | J13-02-246 |  |  |  | Mortex | HRI2000 | HRI2-0031 | 2012-05-03 | 10 | 5 years | In Service | Downlight LED Lamp | J13-02-246-Fan-Lights | Excellent | 1 | Minor Criticality | 2 | Maintain | 1 | No Action | 0 | 0 | 350 | Repaired detatched lamp 17/09/2019
| 2019-09-21 | B10-27501-48 | B10-27501-54 | B10-27501-54 | LOCKSMITH | Bilock Campus | 27501 | Non-Statutory | Evelyn Williams Building | B10 |  |  | B10-- |  |  |  | Bilock | #2500 |  | 2009-09-02 | 15 |  | In Service | 54 campus locks | N/A | Good | 2 | Moderately Critical | 3 | Maintain | 1 | No Action | 0 | 275 | 3000 | Good condition

## 5 - Additions (#)
Tab 4 - Asset Modifications - Used to define modification to the attributes of an existing asset | [24 empty] | Asset Assessment Section - Used when performing asset validation and condition assessments (refer to assessment tables tab)
Additional notes supporting details of information capture, validation, condition assessment (free text field) | Date Asset Information captured (DD/MM/YYYY). | Unique identifier from existing asset register, proposed to be modified (row copied from Tab 9 - Existing Asset Register) | Identifies the Equipment Code of the Parent of this Asset to create an asset hierarchy (ie, for a smoke detector the equipment code for the building FIP would be inserted). If the asset is the parent then copy equipment code in this field | Category, as per Tab 3 - Master Equipment Standards (select this value first from drop down) | Linked to Equipment Standard Category, as per Tab 3 - Master Equipment Standards (select this value after equipment standard category selection, from drop down) | Code linked to equipment standard description as per Tab 3 - Master Equipment Standard (auto generated based on Equipment Standard Category and Equipment Standard Description selections in previous columns) | Type linked to equipment standard description as per Tab 3 - Master Equipment Standard (auto generated based on Equipment Standard Category and Equipment Standard Description selections in previous columns) | Building Name - linked to Building Code (as per space data listing) | Building Code (as per space data listing) | Floor Code (as per space data listing) | Room Code (as per space data listing) | Location (concatenation of the building - floor - room for validation) Automatically generated | For GPS location of external assets (mandatory for all assets external to building rooms) | For GPS location of external assets (mandatory for all assets external to building rooms) | To identify location of Asset within the room (free text field) | Manufacturer of Equipment (free text field) | Model of Equipment (free text field) | Serial Number (free text field) | Estimated date asset was placed in service (DD/MM/YYYY). | Estimated operational life of the asset when originally placed in service (years) | If the asset has a known warranty, state duration (years) | Identifies status of asset as, per Tab 8 - Equipment Status Table (select this value from drop down) | Include all mandatory information, as per Tab 3 - Master Equipment Standards comments column, and any other information that may be useful (free text field) | Confirm photo reference number from folder containing photos of all assets. | Identifies condition of asset, as per Tab 7 - Assessment Tables (select this value from drop down) | Numerical Value (auto generated as per assessment tables tab) | Identifies criticality of asset, as per Tab 7 - Assessment Tables (select this value from drop down) | Numerical Value (auto generated as per assessment tables) | Identifies priority rating of asset, as per Tab 7 - Assessment Tables (select this value from drop down) | Numerical Value (auto generated to suit assessment tables) | Identifiesrecommended actions for asset, as per Tab 7 - Assessment Tables (select this value from drop down) | Numerical Value (auto generated to suit assessment tables) | Estimated cost to bring the Asset back to excellent working condition. ($) | Replacement Value at time of Assessment. ($) | Description of the condition of the Asset and any recommended repairs (free text field)
Notes | Date Information Captured | Equipment Code | Subcomponent Of | Equipment Standard Category | Equipment Standard Description | Equipment Standard | Equipment Code Type | Building Name | Building Code | Floor Code | Room Code | Bulding - Floor - Room | Latitude | Longitude | Asset Location | Manufacturer | Model | Serial Number | In Service Date | Years Life Expectancy | Warranty | Equipment Status | Comments | Photo Ref Number | Condition Rating | Condition Rating (Number) | Criticality Rating | Criticality Rating (Number) | Priority Rating | Priority Rating (Number) | Recommended Action | Recommended Action (Number) | Repair Cost | Replacement Cost | Description
examples | 2019-09-18 | 4003921 | 4001447 | FIRE | Detector - Smk - Aspirating | 12114 | Statutory | Storie Dixson Wing | H10 | 02 | 210 | H10-02-210 |  |  | 2nd clockwise from entrance | NOTIFIER | FSP851AUS |  | 2019-09-11 | 5 | 2 | In Service | Addressable device number: 15283 | H10-02-210-12112-01 | Excellent | 1 | High Criticality | 4 | Code Compliance | 9 | No Action | 0 |  | 300 | New condition (11/09/2019)
| 2019-09-18 | H10-02-225-11124-01 | 2031354 | MECHANICAL | VRV Control Panel | 11124 | Non-Statutory | Storie Dixson Wing | H10 | 02 | 225 | H10-02-225 |  |  | North wall | MITSUBISHI | VRVE18n4 | #156820048 | 2019-09-11 | 15 | 10 | In Service | VRVCP-03 | H10-02-225-11124-01 | Excellent | 1 | Moderately Critical | 3 | Environ. Code | 7 | No Action | 0 |  | 500 | New condition (11/09/2019)
| 2019-09-18 | H10-27501-20 | H10-27501-20 | LOCKSMITH | Bilock Campus | 27501 | Non-Statutory | Storie Dixson Wing | H10 | OSB | RF | H10-OSB-RF |  |  |  | Bilock | #2500 |  | 2019-09-11 | 10 | 2 | In Service | 20 campus locks | N/A | Excellent | 1 | High Criticality | 4 | Mission Support | 6 | No Action | 0 |  | 1000 | New condition (11/09/2019)
| 2019-09-18 | H10-02-210-50012-03 | 1000254 | ICT AV | ICT Projector Screen | 50012 | Non-Statutory | Storie Dixson Wing | H11 | 02 | 210 | H11-02-210 |  |  | Front of lecture hall | Zebra | T230 |  | 2019-09-08 | 20 | 1 | In Service | 3 projector screens, 2x5m | H10-02-210-50012-03 | Excellent | 1 | Minor Criticality | 2 | Company Image | 2 | No Action | 0 |  | 450 | New condition (8/09/2019)
|  |  |  | PLUMBING | Natural Gas Regulator | 16042 | NRM

## 6 - Deactivations (#)
Tab 4 - Asset Modifications - Used to define modification to the attributes of an existing asset
Additional notes supporting details of information capture, validation, condition assessment (free text field) | Date Asset Information captured (DD/MM/YYYY). | Unique identifier from existing asset register, proposed to be modified (row copied from Tab 9 - Existing Asset Register) | Building Code (as per space data listing) | Floor Code (as per space data listing) | Room Code (as per space data listing) | Identifies status of asset as, per Tab 8 - Equipment Status Table (select this value from drop down)
Notes | Date Information Captured | Equipment Code | Building Code | Floor Code | Room Code | Equipment Status
Removed for renovation | 2019-09-23 | 2020333 | A15 | 04 | N412 | Out of Service
Removed for renovation | 2019-09-23 | 2020334 | A15 | 04 | N412 | Out of Service
Removed for renovation | 2019-09-23 | 2009003 | A15 | 04 | N412 | Out of Service
Removed for renovation | 2019-09-23 | A15-04-N400-14305-01 | A15 | 04 | N400 | Out of Service
Removed for renovation | 2019-09-23 | A15-04-N412-14346-01 | A15 | 04 | N412 | Out of Service
Removed for renovation | 2019-09-23 | A15-04-N423-14346-01 | A15 | 04 | N423 | Out of Service
Removed for renovation | 2019-09-23 | A15-04-N431-14346-01 | A15 | 04 | N431 | Out of Service

## 7 - Assesment Tables
Asset Condition Rating Table Mandatory Field - Asset Validation & Condition Assessment
Rating | Status | Description
1 | Excellent | Asset has no Defects; condition and appearance is as new | 1
2 | Good | Asset exhibits superficial wear and tear, minor defects, minor signs of deterioration to surface finishes, does not require major maintenance; no major defects exist | 2
3 | Fair | Asset is in average condition, deteriorated surfaces require attention, services are functional, but require attention; Deferred Maintenance work exists | 3
4 | Poor | Asset has deteriorated badly; serious structural problems; general appearance is poor with eroded protective coatings; elements are defective, services are frequently failing; and a significant number of defects exist. | 4
5 | Unacceptable | Asset has failed; is not operational and is unfit for occupancy or normal use. | 5
Asset Condition Priority Rating Table The asset condition priortiy rating is only used when an issue requiring repair is identified during an asset condition assessment
Rating | Status | Description
1 | Maintain | Regular maintenance required to maintain current state | 1
2 | Company Image | Improvements required to enhance the public image of the University | 2
3 | Def. Renovation | Deferral of repairs or renovations which may eventually lead to major damage to a facility and loss of use, hamper building utilisation or effect economies of operation | 3
4 | Cost Effective | Energy or functional conservation measures with a rapid return on investment | 4
5 | Delayed Priority | Repairs and renovations required, but of less urgency than mission support | 5
6 | Mission Support | Actions required to support functional activities, such as laboratory or workshop equipment that requires repair to be fully functional, or assets that require repair in order to support a productive work environment | 6
7 | Environ. Code | Repairs, renovations and improvements required for long term compliance with local, state or federal environmental regulations | 7
8 | Facility Loss | Repairs, renovations and improvements required to prevent serious facility deterioration and significantly higher costs if not immediately corrected | 8
9 | Code Compliance | Repairs, renovations and improvements required for immediate compliance with local, state or federal building regulations | 9
10 | Life Safety | Hazardous building or site conditions that jeopardise life safety of occupants | 10
Asset Criticality Rating Table (aligned to Risk Management Framework) Mandatory Field - Asset Validation & Condition Assessment Criticality Rating shall take into account impacts to operations safety and environment together with assessment of single point failure, maintainability, reliability and spares lead time, to determine the overall criticality ratings listed below
Rating | Status | Description
1 | Non Critical | Failure of asset is not significant to business operations. Recommend run to fail or basic condition assessment at extended frequencies | 1
2 | Minor Criticality | Failure of asset represents minor consequence to business operations. Recommend basic condition assessment to reduce risk exposure | 2
3 | Moderately Critical | Failure of asset has moderate consequences to business operations.Recommend Preventive Maintenance and basic condition assessments are undertaken to keep asset operational | 3
4 | High Criticality | Critical assets with major consequences to operations if failure occurs. Recommend Preventive Maintenance and detailed condition assessments are performed regularly to reduce risk exposure | 4
5 | Extremely Critical | Critical assets with catastrophic consequences to business if failure occurs. Extensive reliability centred Preventive Maintenance, performance monitoring and detailed condition assessments to be performed at a high frequency to ensure asset remains operational and performance is monitored | 5
Recommended Action Table Manadatory Field - Asset Validation & Condition Assessment
Rating | Status | Description
0 | No Action | No works required to be performed | 0
1 | Clean | Requires cleaning | 1
2 | Adjust | Requires minor adjustments | 2
3 | Remove | Requires removal as it is redundant and no longer in service | 3
4 | Repair | Requires repairs | 4
5 | Replace | Requires replacement as it is past its operational life | 5

## 8 - Equipment Status Table
Tab 8 - Equipment Status Table
Definition | Status Value
Asset has been vacated or left unattended and is no longer being used. The asset is still owned by the enterprise. | Abandoned
Asset is being repaired and is not in service | In Repair
Asset is ready for use or being used | In Service
Asset is being stored and is not in use but is usable | In Storage
Asset is missing | Missing
Asset that is no longer used; is being run minimally or could be out of service for a while. | Out of Service
Asset status is unknown | Unknown

## 9 - Existing Asset Register
Tab 9 - Existing Asset Register for Space and Equipment Category requested